## Info
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
DS Sheet Information
|  | Process Name: | SOFC NG and Coal plant with CCUS
|  | Process Description: | Coal integrated gasification solid oxide fuel cell (SOFC) and natural gas (NG) solid fuel cell power plants with and without carbon capture.
|  | Files: | This unit process is composed of this document and the file, DF_Stage3_SOFC_Power_2015.01.docx, which provides additional details regarding calculations, data quality, and references as relevant.
|  | Summary and Calculations Worksheets: | As shown below, this document contains 3 summary worksheets (Data Summary, Reference Source Info, and DQI) that have been formatted consistent with NETL standards. The remaining 'calculations' worksheets are workspaces used by NETL engineers during the production of this unit process. The 'calculations' worksheets are presented for the convenience of the reader, and have not been subjected to standardized formatting.
This data sheet is organized as follows:
|  | Worksheet | Description
| Summary | Data Summary | Summary of Calculations, Input and Output Flows, Reference Flow, and other information
|  | Parameter Scenarios | Parameters for various scenarios where the unit process is used
|  | Reference Source Info | Referenced citations; citations are referenced by number, listed at the top of the Reference Source Info sheet
|  | DQI | Data Quality Index
| Calculations | scenario 1 (Case 3-7) | Fuel inputs, water use, air emissions, solid waste calculations for IGFC, coal, catalytic gasifier
|  | scenario 2 (Case 1-9) | Fuel inputs, water use, air emissions, solid waste calculations for IGFC, coal traditional gasifier
|  | scenario 3 (Case 3-1) | Fuel inputs, water use, air emissions, solid waste calculations for NGFC, natural gas
|  | scenario 4 (Case 1-6) | Fuel inputs, water use, air emissions, solid waste calculations for IGFC, coal with NG added to syngas
|  | Conversions | Unit Conversions
|  | Assumptions | Assumptions
Date Created:
2015-06-08
Point of Contact:
Timothy Skone (NETL), Timothy.Skone@NETL.DOE.GOV
Revision History:
Original/no revisions
How to Cite This Document:
This document should be cited as: NETL (2015). NETL Life Cycle Inventory Data – Unit Process: SOFC NG and Coal plant with CCUS - Version 01. U.S. Department of Energy, National Energy Technology Laboratory. Retrieved [DATE] from www.netl.doe.gov/LCA
| Additional Notes: | x
|  | For the calculations sheets, values |  | highlighted in yellow |  | are also pulled forward into the 'Data Summary' sheet
Bibliographic references & assumptions referenced by number; see 'Reference Source Info' & 'Assumptions' sheets for cross-reference.
Data Summary sheet color coding: white indicates data input by model engineer; blue indicates automatically calculated values
Abbreviations used throughout this DS:
|  |  |  | SOFC = | Solid Oxide Fuel Cells
|  |  |  | IGFC = | Integrated Gasification Fuel Cell
|  |  |  | NGFC= | Natural Gas Fuel Cell
|  |  |  | PM = | Particulate Matter
Disclaimer:
Template Version:
3.0
Neither the U.S. Department of Energy (DOE) National Energy Technology Laboratory (NETL) nor any person acting on behalf of these organizations:
A. Makes any warranty or representation, express or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that the use of any information, apparatus, method, or process disclosed in this document may not infringe on privately owned rights; or
B. Assumes any liability with this report as to its use, or damages resulting from the use of any information, apparatus, method, or process disclosed in this document.
Reference herein to any specific commercial product, process, or service by trade name, trademark, manufacturer, or otherwise, does not necessarily constitute or imply its endorsement, recommendation, or favoring by NETL. The views and opinions of the authors expressed herein do not necessarily state or reflect those of NETL.

## Data Summary
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
Data Module Summary
Process Name: |  | SOFC NG and Coal plant with CCUS
Reference Flow: |  | 1 | MWh | of | Electricity | [5 empty] | DQI | 2,2,1,1,1 | (see DQI sheet for explanation)
Brief Description: |  | Coal integrated gasification solid oxide fuel cell (SOFC) and natural gas (NG) solid fuel cell power plants with and without carbon capture.
SECTION I: META DATA
Geographical Coverage: |  | USA |  |  | Goal and Scope:
Region |  | Midwest |  |  | Reference Flow: 1 MWh of Electricity
Year Data Best Represents: |  | 2015
Process Type: |  | Energy Conversion (EC) |  |  | This unit process provides a summary of relevant input and output flows associated with integrated gasification fuel cell (IGFC) systems and natural gas fuel cell (NGFC) systems. The first scenario is of an IGFC with catalytic coal gasification. The second is of an IGFC with traditional coal gasification. The third is of an NGFC. The fourth is of an IGFC with natural gas added to the syngas. All coal is assumed to be Illinois #6.
Process Scope: |  | Gate-to-Gate Process (GG)
Allocation Applied: |  | No
Completeness: |  | All Relevant Flows Captured
Flows Aggregated in Data Set: |  |  |  |  | Note: All inputs and outputs are normalized per the reference flow (e.g., per 1MWh of Electricity)
SECTION II: PARAMETERS
This section includes adjustable parameters, calculations needed to support adjustable parameters, and flow calculations based upon adjustable parameters.
| Parameter Name | Formula | Value | Min. Value | Max. Value | Unit | References | Comments
9 | accep_deg |  | 10 |  |  | [percent] | 1,2 | [percent] Percent of fuel cell degradation allowed before replacement
13 | CO2_emissions |  | 9.6615 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] kg CO2 released for every MWh plant output
10 | CO2_saline |  | 634.4396 |  |  | [kg/Mwhnet] | 1,2 | [kg/Mwhnet] mass of CO2 captured for every MWh plant output
13 | coal_flowrate |  | 245.443 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] mass of coal to generate one MWh electricity
10 | fc_degrade |  | 1.5779 |  |  | [%/yr] | 1,2 | [%/yr] number of fuel cells that need replaced every year
5 | HG_em |  | 0 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] mercury emissions to air for every MWh electricity
11 | NG_flowrate |  | 0 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] mass of NG to generate one MWh electricity
9 | net_power |  | 550 |  |  | [MWnet] | 1,3 | [MWnet] net output electricity of plant
6 | NOx_em |  | 0 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] NOx emissions to air for every MWh electricity
5 | PM_em |  | 0 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] PM emissions to air for every MWh electricity
4 | slag |  | 34.7382 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] mass solid slag waste discarded for every one MWh electricity
6 | SO2_em |  | 0 |  |  | [kg/MWhnet] | 1,2 | [kg/MWhnet] SO2 emissions to air for every MWh electricity
13 | wat_discharge |  | 154.4448 |  |  | [L/MWhnet] | 1,2 | [L/MWhnet] water returned to water table for every MWh output
14 | wat_withdrawal |  | 639.2528 |  |  | [L/MWhnet] | 1,2 | [L/MWhnet] water withdrawn from water table for every one MWh electricity
11 | gross_power |  | 653.7 |  |  | [MW] | 1,2 | [MWgross] gross output electricity of plant
10 | cap_factor |  | 90 |  |  | [percent] | 1,2 | [percent] Fraction of the year that the plant is assumed to operate
9 | fc_demand | (fc_degrade/100)/(8766*(cap_factor/100)*net_power)*(100/accep_deg)*gross_power*1000 | 0.016827 |  |  | [kW/MWhnet] | 1,2 | [stacks/MWhnet] Fraction of a fuel cell needed to produce 1 MWh of electricity
8 | fc_waste | fc_demand | 0.016827 |  |  | [kW/MWhnet] | 1,2 | [stacks/MWhnet] Fraction of a fuel cell spent and disposed of per MWh
| End of List | <select this entire row, then insert new row>
SECTION III: INPUT FLOWS
This section includes all input flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
| coal_flowrate | Illinois 6 Coal [Intermediate] | 1 | kg | 245.443 | [kg/MWhnet] | 245.443 | kg | X | Calculated | 1,2 | [Technosphere]
| fc_demand | Solid Oxide Fuel Cells [Intermediate] | 1 | kW | 0.016827 | [kW/MWhnet] | 0.016827 | pcs | X | Calculated | 1,2 | [Technosphere]
| NG_flowrate | Natural Gas [Intermediate] | 1 | kg | 0 | [kg/MWhnet] | 0 | kg | X | Calculated | 1,2 | [Technosphere]
| wat_withdrawal | Water (Unspecified) [Water] | 1 | L | 639.2528 | [L/MWhnet] | 639.2528 | l |  | Calculated | 1,2 | [Resource]
| End of List | <select this entire row, then insert new row> | Factor |  |  |  | Amount |  |  | <select from list>
SECTION IV: OUTPUT FLOWS
This section includes all output flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
|  | Electricity [Energy] | 1 |  | 1 |  | 1 | MWh | X |  |  | Reference flow
| CO2_emissions | Carbon dioxide [Inorganic emissions to air] | 1 | kg | 9.6615 | [kg/MWhnet] | 9.6615 | kg |  | Calculated | 1,2 | Emission to air
| CO2_saline | Carbon dioxide [Intermediate] | 1 | kg | 634.4396 | [kg/Mwhnet] | 634.4396 | kg | X | Calculated | 1,2 | Intermediate product
| HG_em | Mercury (+II) [Heavy metals to air] | 1 | kg | 0 | [kg/MWhnet] | 0 | kg |  | Calculated | 1,2 | Emission to air
| NOx_em | Nitrogen oxides [Inorganic emissions to air] | 1 | kg | 0 | [kg/MWhnet] | 0 | kg |  | Calculated | 1,2 | Emission to air
| PM_em | Dust (unspecified) [Particles to air] | 1 | kg | 0 | [kg/MWhnet] | 0 | kg |  | Calculated | 1,2 | Emission to air
| slag | Waste (solid) [Waste for disposal] | 1 | kg | 34.7382 | [kg/MWhnet] | 34.7382 | kg | * | Calculated | 1,2 | Solid waste
| SO2_em | Sulphur dioxide [Inorganic emissions to air] | 1 | kg | 0 | [kg/MWhnet] | 0 | kg |  | Calculated | 1,2 | Emission to air
| wat_discharge | Water (wastewater) [Water] | 1 | L | 154.4448 | [L/MWhnet] | 154.4448 | L |  | Calculated | 1,2 | emission to water
| fc_waste | Waste (solid) [Waste for disposal] | 1 | kW | 0.016827 | [kW/MWhnet] | 0.016827 | stacks | * | Calculated | 1,2 | Solid waste
| End of List | <select this entire row, then insert new row> | Factor | [6 empty] | <select from list>
Detailed Spreadsheet Lists
| Process Type | Process Scope | Completeness |  |  | Origin |  | Tracked
| <select from list> | <select from list> | <select from list> |  |  | <select from list>
| Extraction Process (EP) | Cradle-to-Grave (End-of-Life) Process (CE) | All Flows Captured |  |  | Measured |  | X
| Manufacturing Process (MP) | Cradle-to-Gate Process (CG) | All Relevant Flows Captured |  |  | Calculated |  | *
| Installation Process (IP) | Gate-to-Gate Process (GG) | Individual Relevant Flows Captured |  |  | Literature
| Basic Process (BP) | Gate-to-Grave (End-of-Life) Process (GE) | Some Relevant Flows Not Captured |  |  | Estimated
| Energy Conversion (EC) |  | No Statement |  |  | No Statement
Transport Process (TP)
Recovery Process (RP)
Waste Treatment Process (WT)
Auxiliary Process (AP)

## PS
Parameter Scenarios
| Parameter Name | Enter a Scenario ID below: | Scenario ID |  |  |  |  | [Units] Comments
|  | 1 | 1 | 2 | 3 | 4 | 5
|  | SOFC NG and Coal plant with CCUS | SOFC NG and Coal plant with CCUS
|  | case 3-7 (2014) | case 3-7 (2014) | case 1-9 (2014) | case 3-1 (2015) ccs | case 3-1(2015) no ccs | case 1-6 (2014)
4 | accep_deg | 10 | 10 | 10 | 10 | 10 | 10 | [percent] Percent of fuel cell degradation allowed before replacement
5 | CO2_emissions | 9.6615 | 9.6615 | 11.4759 | 5.8967 | 239.6328 | 9.6162 | [kg/MWhnet] kg CO2 released for every MWh plant output
6 | CO2_saline | 634.4396 | 634.4396 | 808.2303 | 294.835 | 0 | 631.4611 | [kg/Mwhnet] mass of CO2 captured for every MWh plant output
7 | coal_flowrate | 245.443 | 245.443 | 287.5047 | 0 | 0 | 168.675 | [kg/MWhnet] mass of coal to generate one MWh electricity
8 | cap_factor | 90 | 90 | 90 | 85 | 85 | 85 | [percent] Fraction of the year that the plant is assumed to operate
9 | fc_degrade | 1.5779 | 1.5779 | 1.5779 | 1.4902 | 1.4902 | 1.4902 | [%/yr] number of fuel cells that need replaced every year
10 | HG_em | 0 | 0 | 0 | 0 | 0 | 0 | [kg/MWhnet] mercury emissions to air for every MWh electricity
11 | NG_flowrate | 0 | 0 | 0 | 106.15 | 99.3534 | 44.7871 | [kg/MWhnet] mass of NG to generate one MWh electricity
12 | net_power | 550 | 550 | 550.1 | 550.058 | 550.136 | 550.2 | [MWnet] net output electricity of plant
13 | NOx_em | 0 | 0 | 0 | 0 | 0 | 0 | [kg/MWhnet] NOx emissions to air for every MWh electricity
14 | PM_em | 0 | 0 | 0 | 0 | 0 | 0 | [kg/MWhnet] PM emissions to air for every MWh electricity
15 | slag | 34.7382 | 34.7382 | 23.7702 | 0 | 0 | 13.9458 | [kg/MWhnet] mass solid slag waste discarded for every one MWh electricity
16 | SO2_em | 0 | 0 | 0 | 0 | 0 | 0 | [kg/MWhnet] SO2 emissions to air for every MWh electricity
17 | gross_power | 653.7 | 653.7 | 696.7 | 601.1 | 563.7 | 658.1 | [MWgross] gross output electricity of plant
18 | wat_discharge | 154.4448 | 154.4448 | 228.7349 | 151.5381 | 70.4087 | 191.1282 | [L/MWhnet] water returned to water table for every MWh output
19 | wat_withdrawal | 639.2528 | 639.2528 | 841.4473 | 462.4597 | 320.2458 | 653.8814 | [L/MWhnet] water withdrawn from water table for every one MWh electricity
Scenario Descriptions:
| Scenario ID | Description
| 1 | IGFC, coal, catalytic gasifier
| 2 | IGFC, coal traditional gasifier
| 3 | NGFC, natural gas, with ccs
| 4 | NGFC, natural gas, no ccs
| 5 | IGFC, coal with NG added to syngas
The purpose of this "Parameters Scenarios" worksheet is to provide a flexible method for adjusting parameters within this unit process. The above table allows you to select a scenario ID (CELL C4) and uses a lookup function to populate the adjustable parameters (the cells with yellow shading). The values for the adjustable parameters are linked to the "Data Summary" sheet.

## Reference Source Info
Field Name
Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
SourceType | Separate Publication | Separate Publication
Title | Techno-Economic Analysis of Integrated Gasification Fuel Cell Systems Created by Energy Sector Planning and Analysis for SEAP & OPPB | Technoeconomic Analysis of Natural Gas Fuel Cell Plant Configurations
FirstAuthor | NETL | NETL
AdditionalAuthors
Year | 2014 | 2015
Date | November 24 | April 8
PlaceOfPublication
Publisher
PageNumbers
Table or Figure Number
NameOfEditors
TitleOfAnthology
Journal
VolumeNo
IssueNo
Docket Number
Copyright
Internet Address
Internet Access Date
Data Type (Origin)
Year Data Represents
Geographical Representation | USA | USA
Representativeness
BibliographicText | National Energy Technology Laboratory, 2014. Techno-Economic Analysis of Integrated Gasification Fuel Cell Systems Created by Energy Sector Planning and Analysis for SEAP & OPPB. | National Energy Technology Laboratory, 2015. Technoeconomic Analysis of Natural Gas Fuel Cell Plant Configurations.
Text/Description | Scenarios 1, 2 and 5 plant configuation data | Scenarios 3 and 4 plant configuration data
Reference Source Info Lists
Source Type
<select from list>
Undefined
Article
Chapters in Anthology
Separate Publication
Measurement on Site
Oral Communication
Personal Written Communication
Questionnaires

## DQI
Data Quality Index
DQI Determination
| Input/Output | Reference (see 'Reference Source Info' worksheet) | Source Reliability | Completeness | Temporal Correlation | Geographical Correlation | Technical Correlation | DQI | Recommendations | Determinations
| CO2 air emissions, Captured CO2, Illinois 6 coal, solid oxide fuel cells, mercury air emissions, natural gas, NOx air emissions, PM emissions, solid waste, water discharge, water withdrawal | 1,2 | 2 | 2 | 1 | 1 | 1 | 2,2,1,1,1 | Requirements met | OK
[8 empty] | 0,0,0,0,0 | Requirements met | OK
[8 empty] | 0,0,0,0,0 | Requirements met | OK
[8 empty] | 0,0,0,0,0 | Requirements met | OK
| Total | [6 empty] | 2,2,1,1,1
DQI Methodology
DQI Matrix (from NETL LCI&C Guideline Document, adapted from Weidema and Wenaes)
| Indicator | Score
|  | 1 | 2 | 3 | 4 | 5
| Source Reliability (for most applications, source quality guidelines only factor) | data verified based on measurements | data verified based on some assumptions and/or standard science and engineering calculations | data verified with many assumptions, or non-verified but from quality source | qualified estimate | non-qualified estimate
|  | source quality guidelines met |  | source quality guidelines not met
|  | data cross checks, greater than or equal to 3 quality sources | 2 or less data sources available for cross check, or data sources available that do not meet quality standards |  | no data available for cross check
| Completeness | representative data from a sufficient sample of sites over an adequate period of time | smaller number of site but an adequate period of time | sufficient number of sites but a less adequate period of time | smaller number of sites and shorter periods or incomplete data from an adequate number of sites or periods | representativeness unknown or incomplete data sets
| Temporal Correlation | less than three years of difference to year of study/current year | less than 6 years of difference | less than 10 years difference | less than 15 years difference | age of data unknown or more than 15 years difference
| Geographical Correlation | data from area under study | average data from larger area or specific data from a close area | data from area with similar production conditions | data from area with slightly similar production conditions | data from unknown area or area with very different production conditions
| Technological Correlation | data from technology, process or materials being studied | data from a different technology using the same process and/or materials |  | data on related process or material using the same technology | data or related process or material using a different technology
Indicator Descriptions
Source Reliability -- This indicator relates to the quality of the data source and the verification of the data collection methods used within the source.
Data Verification -- Source data that have been verified within error bounds by either the source author (with a high level of transparency) or the LCI modeler. Verification can be done by measurement, including on-site checking, recalculation, or mass or energy balance analysis. If the source data cannot be verified without making assumptions (i.e., not enough data are available to close the mass/energy balance), then the score should be a 2 or 3, depending on the number of assumptions. If no source data are available, a qualified estimate from an expert in the field should receive a score of 4, and an estimate from a non-expert should receive a score of 5. Mostly applicable to primary data.
Source Quality Guidelines -- The highest quality source should be
o From a peer reviewed journal or a government sponsored study. If the source is an LCA, it must meet ISO requirements.
o Publicly available either for free or at cost, or directly representative of the process of interest.
o Written/published by an unbiased party.
o An unbiased survey of experts or process locations.
When the source used for data is a reputable model that does not specifically meet the above criteria, it is the discretion of the modeler to determine the rank of the source. An example for justification would be if the data have been used in published reports that met the data quality standards.
Data Cross-Check -- The number of sources that verify the same data point or series, within reason. As a general benchmark, a high standard is greater than or equal to three data cross checks with quality approved sources. This typically refers to primary data, and if no other data sources are available, this can be omitted.
Completeness -- This indicator quantifies the statistical robustness of the source data. This ranking is based on how many data points were taken, how representative the sample is to the studied process, and whether the data were taken for an acceptable time period to even out normal process fluctuations. The following examples are given to help clarify this indicator.
Temporal Correlation -- This indicator represents how well the time period in which the data were collected corresponds with the year of the study. If the study is set to evaluate the use of a technology from 2000 to 2040, data from 1970 would not be very accurate. It is important when assigning this ranking to take notice of any discrepancies between the year the source was published and the year(s) the data were collected.
Geographical Correlation -- This indicator represents the appropriateness between the region of study and the source data region. This indicator becomes important when comparing data from different countries. For example, technological advances might reasonably be expected to develop differently in different countries, so efficiency and energy use might be very different. This is also important when looking at best management practices for carbon mitigation.
Technological Correlation -- This indicator embodies all other differences that may be present between the study goals and the data source. From the above example, using data for a type of biomass that is not being studied in the LCA should result in a lower technological representativeness ranking.
Steps for Applying DQM
1) Calculate score for each unit process (UP) input. If more than one reference source is used for one input, and the score is lower, consider both scores. If an indicator does not relate to a specific source, assume N/A. If all emissions come from one source, only one score is needed
- when a score is determined for a particular reference source, add to 'Reference Source Info' for future use
2) From the reference scores, determine the data quality indicator (DQI) for the unit process inputs for commissioning/decommissioning operations (when applicable)*
- the scores are not additive, rather, the lowest score for an indicator of a particular data input is the lowest score for the UP
3) Significant inputs of low quality unit processes (DQI mostly 3-5) should be varied to the minimum and maximum values or 95 percent confidence interval of the uncertainty range.
- check significance first. If the input is not significant by a long shot (or with the maximum possible value), it is not necessary to include in the UP
4) If the change in the final result from a single unit process is greater than a threshold value, for example, 0.1 g CO2e/MJ, then the processes should be flagged for possible additional data quality refinement
- for example, if emissions from the total steel inputs are found to be significant during sensitivity, the DQI will be performed on the steel profile. If this is not possible (because data are not transparent/purchased), it will be listed as a future recommendation
- if, however, the steel inputs are significant due to a large amount of steel needed for a particular process, then the DQI on that input should be performed and the data refined if needed
5) If the UP input is significant (with or without sensitivity), but no data refinement is possible, this is listed as a data limitation and noted in the report
* For NETL LCI&C studies, because data quality for construction is typically low, sensitivity on those inputs is already performed and the DQI does not need to be calculated. If sensitivity is not performed on construction, or sensitivity shows that a particular input is significant, then the DQI will be performed

## scenario 1 (Case 3-7)
Scenario 1 Calculations
Calculations | [Yellow-highlight cells are carried to data summary] |  |  |  |  | References
[7 empty] | CASE | 3-1 | 3-2 | 3-3 | 3-4 | 3-5 | 3-6 | 3-7
Flow | Value | Units | Notes | Assumptions |  |  | Dry Syngas CH4 Content (%) | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
With CCS
CO2 emissions | 21.3 | lb/MWhnet |  |  |  | [1] | SOFC Degradation Rate (%/1000 h) | 1.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
CO2 emissions | 9.6615 | kg/MWhnet | Emissions per net MWh |  |  |  | SOFC Overpotential (mV) | 140 | 140 | 70 | 70 | 70 | 70 | 70
CO2 captured | 634.4396 | kg/MWhnet | captured CO2 per net MWh |  |  |  | Capacity Factor (%) | 80 | 80 | 80 | 85 | 90 | 90 | 90
Gross Power Output | 653.7 | MWgross | Gross power output for 1 hour |  |  | [1] | SOFC Stack Cost ($/kW) | 225 | 225 | 225 | 225 | 225 | 200 | 200
Net Power Output | 550 | MWnet | Net power output for 1 hour |  |  | [1] | Inverter Efficiency (%) | 97 | 97 | 97 | 97 | 97 | 97 | 98
Coal Flowrate | 297610 | lb/hr |  |  |  | [1] | PERFORMANCE
Coal Flowrate | 134993.6252 | kg/hr |  |  |  |  | SOFC Cell Voltage | 0.796 | 0.796 | 0.862 | 0.862 | 0.862 | 0.862 | 0.862
Coal Flowrate | 245.443 | kg/MWhnet | Emissions per net MWh |  |  |  | Gross Power (MWe) | 668.9 | 668.9 | 654.8 | 654.8 | 654.8 | 654.8 | 653.7
Natural Gas Flowrate | 0 | lb/hr |  |  |  | [1] | Auxiliary Loads (MWe) | 118.6 | 118.6 | 104.7 | 104.7 | 104.7 | 104.7 | 103.7
Natural Gas Flowrate | 0 | kg/hr |  |  |  |  | Net Power (MWe) | 550.3 | 550.3 | 550.1 | 550.1 | 550.1 | 550.1 | 550
Natural Gas Flowrate | 0 | kg/MWhnet | Emissions per net MWh |  |  |  | Coal Flowrate (lb/hr) | 329238 | 329238 | 300800 | 300800 | 300800 | 300800 | 297610
Raw water withdrawal | 1548 | gpm |  |  |  | [1] | NG Flowrate (lb/hr) | - | - | - | - | - | - | -
Raw water withdrawal | 168.8727 | gal/MWhnet |  |  |  |  | Net Electric Efficiency, HHV (%) | 48.9 | 48.9 | 53.5 | 53.5 | 53.5 | 53.5 | 54.1
Raw water withdrawal | 639.2528 | L/MWhnet | Consumption per net MWh |  |  |  | Net Plant Heat Rate, HHV (Btu/kWh) | 6980 | 6980 | 6380 | 6380 | 6380 | 6380 | 6312
Raw water discharge | 374 | gpm |  |  |  | [1] | CO2 Capture rate (%) | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
Raw water discharge | 40.8 | gal/MWhnet |  |  |  |  | CO2 Emissions (lb/MWhgross) | 20.5 | 20.5 | 18.1 | 18.1 | 18.1 | 18.1 | 17.9
Raw water discharge | 154.4448 | L/MWhnet |  |  |  |  | CO2 Emissions (lb/MWhnet) | 25 | 25 | 21.5 | 21.5 | 21.5 | 21.5 | 21.3
slag | 19106 | kg/hr |  |  |  | [1] | Raw Water Consumption (gpm/MWnet) | 2.4 | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1
slag | 34.7382 | kg/MWhnet |  |  |  |  | COST
[7 empty] | Total Plant Cost (TPC) (1000$) | 1146491 | 1146491 | 1074226 | 1074226 | 1074226 | 1059099 | 1052954
Fuel cell life | [6 empty] | Total Overnight Cost (TOC) (1000$) | 1423360 | 1423360 | 1333965 | 1333814 | 1333680 | 1315498 | 1307827
Capacity factor | 90 | % |  |  |  | [1] | Total As-Spent Cost (TASC) (1000$) | 1622631 | 1622631 | 1520720 | 1520548 | 1520395 | 1499668 | 1490922
Operation hours per year | 7889.4 | hrs/yr |  |  |  |  | Cost of Electricity ($/MWh)
% Fuel cell degradation per year | 1.5779 | %/yr |  |  |  |  | Variable COE | 83.9 | 34.6 | 32.6 | 31.9 | 31.3 | 30.9 | 30.7
Percent acceptable degradation | 10 | % |  |  |  |  | Fuel | 20.4 | 20.4 | 18.6 | 18.6 | 18.6 | 18.6 | 18.4
Years of fuel cell operation | 6.3376 | yrs |  |  |  |  | Variable O&M | 63.6 | 14.2 | 14 | 13.3 | 12.7 | 12.3 | 12.2
Alternative formula | 3.6364e-08 | fuel cell/MWh |  |  |  |  | Fixed O&M | 12.4 | 12.4 | 12.1 | 11.4 | 10.7 | 10.7 | 10.6
number of stacks | 42 | count |  |  |  | [1] | Capital Charges | 45.9 | 45.9 | 43 | 40.5 | 38.2 | 37.7 | 37.5
Other air emissions | [6 empty] | Total First Year COE (excluding T&S) | 142.3 | 92.9 | 87.7 | 83.8 | 80.3 | 79.3 | 78.8
SO2 | 0 | kg/MWhnet |  |  |  | [1] | CO2 T&S | 6.5 | 6.5 | 6 | 6 | 6 | 6 | 5.9
NOx | 0 | kg/MWhnet |  |  |  | [1] | Total First Year COE (including T&S) | 148.8 | 99.5 | 93.7 | 89.7 | 86.2 | 85.3 | 84.7
PM | 0 | kg/MWhnet |  |  |  | [1] | NETL Metrics
HG | 0 | kg/MWhnet |  |  |  | [1] | % COE reduction | -7 | 30.1 | 34.1 | 37 | 39.6 | 40.4 | 40.8
[7 empty] | (COEIGFC - COE IGCC with CCS)/ COEIGCC with CCS | -7 | 30.1 | 34.1 | 37 | 39.6 | 40.4 | 40.8
[7 empty] | Cost of Captured CO2 ($/tonne CO2) | 113.2 | 30.1 | 23.2 | 16 | 9.5 | 7.8 | 6.9
[7 empty] | (COEIGFC - COEAUSC PC)/ CO2 Captured (tonnes/MWh) | 113.2 | 30.1 | 23.2 | 16 | 9.5 | 7.8 | 6.9

## scenario 2 (Case 1-9)
Scenario 2 Calculations
Calculations | [Yellow-highlight cells are carried to data summary] |  |  |  |  | References
[7 empty] | CASE | 1-1 | 1-2 | 1-3 | 1-4 | 1-5 | 1-6 | 1-7 | 1-8 | 1-9
Flow | Value | Units | Notes | Assumptions |  |  | SOFC Degradation Rate (%/1000 h) | 1.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
With CCS | [6 empty] | SOFC Overpotential (mV) | 140 | 140 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CO2 emissions | 25.3 | lb/MWhnet |  |  |  | [1] | Capacity Factor (%) | 80 | 80 | 80 | 85 | 85 | 85 | 90 | 90 | 90
CO2 emissions | 11.4759 | kg/MWhnet | Emissions per net MWh |  |  |  | Dry Syngas CH4 Content (%) | 5.8 | 5.8 | 5.8 | 5.8 | 10.8 | 24.6 | 10.8 | 10.8 | 10.8
CO2 captured | 808.2303 | kg/MWhnet | captured CO2 per net MWh |  |  |  | SOFC Stack Cost ($/kW) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 200 | 200
Gross Power Output | 696.7 | MWgross | Gross power output for 1 hour |  |  | [1] | Inverter Efficiency (%) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 98
Net Power Output | 550.1 | MWnet | Net power output for 1 hour |  |  | [1] | PERFORMANCE
Coal Flowrate | 348675 | lb/hr |  |  |  | [1] | SOFC Cell Voltage | 0.816 | 0.816 | 0.885 | 0.885 | 0.877 | 0.866 | 0.877 | 0.877 | 0.877
Coal Flowrate | 158156.3196 | kg/hr |  |  |  |  | Gross Power (MWe) | 729.9 | 729.9 | 713.8 | 713.8 | 698.2 | 658.1 | 698.2 | 698.2 | 696.7
Coal Flowrate | 287.5047 | kg/MWhnet | Emissions per net MWh |  |  |  | Auxiliary Loads (MWe) | 179.9 | 179.9 | 163.7 | 163.7 | 148 | 107.9 | 148 | 148 | 146.6
Natural Gas Flowrate | 0 | lb/hr |  |  |  | [1] | Net Power (MWe) | 550 | 550 | 550.1 | 550.1 | 550.2 | 550.2 | 550.2 | 550.2 | 550.1
Natural Gas Flowrate | 0 | kg/hr |  |  |  |  | Coal Flowrate (lb/hr) | 406900 | 406900 | 378000 | 378000 | 352250 | 204600 | 352250 | 352250 | 348675
Natural Gas Flowrate | 0 | kg/MWhnet | Emissions per net MWh |  |  |  | NG Flowrate (lb/hr) | - | - | - | - | - | 54326 | - | - | -
Raw water withdrawal | 2038 | gpm |  |  |  | [1] | Net Electric Efficiency, HHV (%) | 39.5 | 39.5 | 42.6 | 42.6 | 45.7 | 51.9 | 45.7 | 45.7 | 46.1
Raw water withdrawal | 222.2869 | gal/MWhnet |  |  |  |  | Net Plant Heat Rate, HHV (Btu/kWh) | 8630 | 8630 | 8017 | 8017 | 7468 | 6569 | 7468 | 7468 | 7394
Raw water withdrawal | 841.4473 | L/MWhnet | Consumption per net MWh |  |  |  | CO2 Capture rate (%) | 98.6 | 98.6 | 98.6 | 98.6 | 98.6 | 98.5 | 98.6 | 98.6 | 98.6
Raw water discharge | 554 | gpm |  |  |  | [1] | CO2 Emissions (lb/MWhgross) | 23.6 | 23.6 | 21.5 | 21.5 | 20.1 | 17.8 | 20.1 | 20.1 | 19.9
Raw water discharge | 60.4254 | gal/MWhnet |  |  |  |  | CO2 Emissions (lb/MWhnet) | 31.3 | 31.3 | 27.9 | 27.9 | 25.5 | 21.2 | 25.5 | 25.5 | 25.3
Raw water discharge | 228.7349 | L/MWhnet |  |  |  |  | Raw Water Consumption (gpm/MWnet) | 2.3 | 2.3 | 2 | 2 | 2.7 | 2 | 2.7 | 2.7 | 2
slag | 13076 | kg/hr |  |  |  | [1] | COST
slag | 23.7702 | kg/MWhnet |  |  |  |  | Total Plant Cost (TPC) (1000$) | 1620361 | 1620361 | 1531544 | 1531544 | 1450569 | 1166265 | 1450569 | 1435438 | 1426949
[7 empty] | Total Overnight Cost (TOC) (1000$) | 1997000 | 1997000 | 1887644 | 1887524 | 1787666 | 1432881 | 1787561 | 1769373 | 1758854
Fuel cell life | [6 empty] | Total As-Spent Cost (TASC) (1000$) | 2276579 | 2276579 | 2151914 | 2151777 | 2037939 | 1633485 | 2037820 | 2017085 | 2005093
Capacity factor | 90 | % |  |  |  | [1] | Cost of Electricity ($/MWh)
Operation hours per year | 7889.4 | hrs/yr |  |  |  |  | Variable COE | 83.8 | 37.4 | 35.5 | 34.9 | 33.2 | 37 | 32.7 | 32.3 | 32
% Fuel cell degradation per year | 1.5779 | %/yr |  |  |  |  | Fuel | 25.4 | 25.4 | 23.6 | 23.6 | 22 | 26.4 | 22 | 22 | 21.7
Percent acceptable degradation | 10 | % |  |  |  |  | Variable O&M | 58.4 | 12 | 11.9 | 11.3 | 11.2 | 10.6 | 10.7 | 10.3 | 10.3
Years of fuel cell operation | 6.3376 | yrs |  |  |  |  | Fixed O&M | 13.6 | 13.6 | 13.1 | 12.3 | 11.9 | 10.5 | 11.3 | 11.2 | 11.2
Alternative formula | 3.6364e-08 | fuel cell/MWh |  |  |  |  | Capital Charges | 64.4 | 64.4 | 60.9 | 57.3 | 54.2 | 43.5 | 51.2 | 50.7 | 50.4
number of stacks | 42 | count |  |  |  | [1] | Total First Year COE (excluding T&S) | 161.7 | 115.3 | 109.4 | 104.5 | 99.3 | 91 | 95.2 | 94.2 | 93.6
Other air emissions | [6 empty] | T&S | 8.4 | 8.4 | 7.8 | 7.8 | 7.3 | 5.5 | 7.3 | 7.3 | 7.2
SO2 | 0 | kg/MWhnet |  |  |  | [1] | Total First Year COE (including T&S) | 170.2 | 123.8 | 117.3 | 112.3 | 106.6 | 96.5 | 102.4 | 101.5 | 100.8
NOx | 0 | kg/MWhnet |  |  |  | [1] | NETL Metrics
PM | 0 | kg/MWhnet |  |  |  | [1] | % COE reduction | -21.6 | 13.3 | 17.7 | 21.4 | 25.3 | 31.6 | 28.5 | 29.2 | 29.6
HG | 0 | kg/MWhnet |  |  |  | [1] | (COEIGFC - COE IGCC with CCS)/ COEIGCC with CCS | -21.6 | 13.3 | 17.7 | 21.4 | 25.3 | 31.6 | 28.5 | 29.2 | 29.6
[7 empty] | Cost of Captured CO2 ($/tonne CO2) | 113 | 52.5 | 48.2 | 41.2 | 36.5 | 31.7 | 30.2 | 28.8 | 28.2
[7 empty] | (COEIGFC - COEAUSC PC)/ CO2 Captured (tonnes/MWh) | 113 | 52.5 | 48.2 | 41.2 | 36.5 | 31.7 | 30.2 | 28.8 | 28.2

## Scenario 3 (Case 3-1) ccs
Scenario 3 Calculations
Calculations | [Yellow-highlight cells are carried to data summary] |  |  |  |  | References
Exhibit 6‑6 Case 3-1 - IR- NGFC plant with and without CCS - Performance Summary
Flow | Value | Units | Notes | Assumptions |  |  | Carbon Capture | With CCS | No CCS
With CCS | [6 empty] | POWER SUMMARY (Gross Power at Generator Terminals, kWe)
CO2 emissions | 13 | lb/MWhnet |  |  |  | [2] | SOFC Power | 537600 | 503300
CO2 emissions | 5.8967 | kg/MWhnet | Emissions per net MWh |  |  |  | Natural Gas/Syn Gas Expander Power | - | -
CO2 captured | 294.835 | kg/MWhnet | captured CO2 per net MWh |  |  |  | Steam Turbine Power | 63500 | 60400
Gross Power Output | 601.1 | MWgross | Gross power output for 1 hour |  |  | [2] | TOTAL GROSS POWER (kWe) | 601100 | 563700
Net Power Output | 550.058 | MWnet | Net power output for 1 hour |  |  | [2] | AUXILIARY LOAD SUMMARY, kWe
Coal Flowrate | 0 | lb/hr |  |  |  | [2] | Air Separation Unit Auxiliaries | 144 | -
Coal Flowrate | 0 | kg/hr |  |  |  |  | Air Separation Unit Main Air Compressor | 6680 | -
Coal Flowrate | 0 | kg/MWhnet | Emissions per net MWh |  |  |  | Oxygen Compressor | - | -
Natural Gas Flowrate | 128725 | lb/hr |  |  |  | [2] | CO2 Compression | 16000 | -
Natural Gas Flowrate | 58388.6778 | kg/hr |  |  |  |  | CO2 Purification | 12554 | -
Natural Gas Flowrate | 106.15 | kg/MWhnet | Emissions per net MWh |  |  |  | Boiler Feedwater Pumps | 1102 | 1048
Raw water withdrawal | 1120 | gpm |  |  |  | [2] | Condensate Pump | 82 | 78
Raw water withdrawal | 122.1689 | gal/MWhnet |  |  |  |  | Circulating Water Pump | 1590 | 760
Raw water withdrawal | 462.4597 | L/MWhnet | Consumption per net MWh |  |  |  | Cooling Tower Fans | 830 | 390
Raw water discharge | 367 | gpm |  |  |  | [2] | Steam Turbine Auxiliaries | 26 | 25
Raw water discharge | 40.0321 | gal/MWhnet |  |  |  |  | Cathode Air Blower | 4050 | 3450
Raw water discharge | 151.5381 | L/MWhnet |  |  |  |  | Cathode Recycle Blower | 3870 | 3920
slag | 0 | kg/hr |  |  |  | [2] | Anode Recycle Blower | 1830 | 1850
slag | 0 | kg/MWhnet |  |  |  |  | Miscellaneous Balance of Plant2 | 344 | 322
[7 empty] | Transformer Losses | 1940 | 1720
Fuel cell life | [6 empty] | TOTAL AUXILIARIES, kWe | 51042 | 13564
Capacity factor | 85 | % |  |  |  | [2] | NET POWER, kWe | 550058 | 550136
Operation hours per year | 7451.1 | hrs/yr |  |  |  |  | NET PLANT EFFICIENCY, % (HHV) | 64.7 | 69.1
% Fuel cell degradation per year | 1.4902 | %/yr |  |  |  | [2] | NET PLANT HEAT RATE, kJ/kWh (Btu/kWh) | 5,567 (5,277) | 5,211 (4,939)
Percent acceptable degradation | 10 | % |  |  |  |  | CO2 Capture Rate (%) | 98 | 0
Years of fuel cell operation | 6.7104 | yrs |  |  |  |  | CONDENSER COOLING DUTY 106 kJ/h (106 Btu/h) | 369 (350) | 348 (330)
Alternative formula | 3.6364e-08 | fuel cell/MWh |  |  |  |  | Natural Gas Feed Rate, kg/h (lb/h) | 58,389 (128,725) | 54,658 (120,500)
number of stacks | 42 | count |  |  |  | [2] | Thermal Input1, kWt | 850673 | 796319
Other air emissions | [6 empty] | Raw Water Withdrawal, m3/min (gpm) | 4.2 (1,120) | 2.9 (778)
SO2 | 0 | kg/MWhnet |  |  |  | [2] | Raw Water Consumption, m3/min (gpm) | 2.9 (754) | 2.3 (606)
NOx | 0 | kg/MWhnet |  |  |  | [2]
PM | 0 | kg/MWhnet |  |  |  | [2]
HG | 0 | kg/MWhnet |  |  |  | [2]

## Scenario 4 (Case 3-1) no ccs
Scenario 4 Calculations
Calculations | [Yellow-highlight cells are carried to data summary] |  |  |  |  | References | Without CCS
[7 empty] | CASE |  | 1-0 | 1-1 | 1-4 | 2-1 | 3-1
Flow | Value | Units | Notes | Assumptions |  |  | SOFC Stack Cost ($/kW) |  | 225
Without CCS | [6 empty] | External Reformation (%) |  | 100 | 40 |  |  | 0
CO2 emissions | 528.3 | lb/MWhnet |  |  |  | [2] | SOFC Degradation Rate (%/1000 h) |  | 1.5 |  | 0.2
CO2 emissions | 239.6328 | kg/MWhnet | Emissions per net MWh |  |  |  | SOFC Overpotential (mV) |  | 140 |  | 70
CO2 captured | 0 | kg/MWhnet | captured CO2 per net MWh |  |  |  | Capacity Factor (%) |  | 80 |  | 85
Gross Power Output | 563.7 | MWgross | Gross power output for 1 hour |  |  | [2] | Inverter Efficiency (%) |  | 97 |  |  | 98
Net Power Output | 550.136 | MWnet | Net power output for 1 hour |  |  | [2] | SOFC Operating Pressure |  | Atmospheric |  |  | Pressurized (285 psia) | Atmospheric
Coal Flowrate | 0 | lb/hr |  |  |  | [2] |  |  | (15.6 psia) |  |  |  | (15.6 psia)
Coal Flowrate | 0 | kg/hr |  |  |  |  | PERFORMANCE
Coal Flowrate | 0 | kg/MWhnet | Emissions per net MWh |  |  |  | SOFC (Parameters) | Cell Voltage | 0.889 | 0.871 | 0.797 | 0.915 | 0.829
Natural Gas Flowrate | 120500 | lb/hr |  |  |  | [2] |  | Average Nernst Voltage (V) | 0.899 | 0.899 | 0.896 | 0.953 | 0.883
Natural Gas Flowrate | 54657.8806 | kg/hr | [5 empty] | In-stack FU (%) | 80.4 | 80 | 80 | 80 | 79
Natural Gas Flowrate | 99.3534 | kg/MWhnet | Emissions per net MWh |  |  |  | Gross Power (kWe) |  | 587600 | 573400 | 568700 | 638500 | 563700
Raw water withdrawal | n/a | gpm |  |  |  | [2] | Auxiliary Loads (kWe) |  | 37521 | 23381 | 18433 | 88413 | 13564
Raw water withdrawal | 84.6 | gal/MWhnet |  |  |  |  | Air Separation Unit (kWe) |  | 8180 | 2800 | 2630 | 13450 | -
Raw water withdrawal | 320.2458 | L/MWhnet | Consumption per net MWh |  |  |  | CO2 Drying, Purification and Compression (CPU) (kWe) |  | - | - | - | - | -
Raw water discharge | n/a | gpm |  |  |  | [2] | Blowers (kWe) |  | 22890 | 15450 | 11190 | 71428 | 9220
Raw water discharge | 18.6 | gal/MWhnet |  |  |  |  | Steam Cycle and Miscellaneous (kWe) |  | 6451 | 5131 | 4613 | 1375 | 4344
Raw water discharge | 70.4087 | L/MWhnet |  |  |  |  | Net Power (kWe) |  | 550079 | 550019 | 550267 | 550087 | 550136
slag | 0 | kg/hr |  |  |  | [2] | NG Flowrate (lb/hr) |  | 159542 | 136500 | 128350 | 124000 | 120500
slag | 0 | kg/MWhnet |  |  |  |  | Net Electric Efficiency, HHV (%) |  | 52.2 | 61 | 64.9 | 67.1 | 69.1
[7 empty] | Net Plant Heat Rate, HHV (Btu/kWh) |  | 6540 | 5596 | 5260 | 5083 | 4939
Fuel cell life | [6 empty] | CO2 Capture rate (%) |  | 0 | 0 | 0 | 67.1 | 0
Capacity factor | 85 | % |  |  |  | [2] | CO2 Captured (tonnes per year) |  | 0 | 0 | 0 | 0 | 0
Operation hours per year | 7451.1 | hrs/yr |  |  |  |  | CO2 Emissions (lb/MWhgross) |  | 657.9 | 575.6 | 544.8 | 469.5 | 515.6
% Fuel cell degradation per year | 1.4902 | %/yr |  |  |  |  | CO2 Emissions (lb/MWhnet) |  | 702.8 | 600.1 | 563 | 545 | 528.3
Percent acceptable degradation | 10 | % |  |  |  |  | Raw Water Withdrawal (gpm/MWnet) |  | 3.14 | 2.03 | 1.73 | 0.83 | 1.41
Years of fuel cell operation | 6.7104 | yrs |  |  |  |  | Raw Water Consumption (gpm/MWnet) |  | 2.58 | 1.63 | 1.39 | 0.69 | 1.1
Alternative formula | 3.6364e-08 | fuel cell/MWh |  |  |  |  | COST
number of stacks | 42 | count |  |  |  | [2] | Total Plant Cost (TPC) (1000$) |  | 684202 | 578613 | 541241 | 710436 | 477729
Other air emissions | [6 empty] | Total Overnight Cost (TOC) (1000$) |  | 835811 | 705590 | 660405 | 863357 | 581919
SO2 | 0 | kg/MWhnet |  |  |  | [2] | Total As-Spent Cost ((TASC) 1000$) |  | 952825 | 804373 | 752862 | 984227 | 663388
NOx | 0 | kg/MWhnet |  |  |  | [2] | Cost of Electricity ($/MWh)
PM | 0 | kg/MWhnet |  |  |  | [2] | Variable COE |  | 94.6 | 91.6 | 40.4 | 42.2 | 37.9
HG | 0 | kg/MWhnet |  |  |  | [2] | Fuel |  | 40.1 | 34.3 | 32.2 | 31.2 | 30.3
[7 empty] | Variable O&M |  | 54.5 | 57.3 | 8.1 | 11.1 | 7.6
[7 empty] | Fixed O&M |  | 6.1 | 5.6 | 5 | 5.9 | 4.7
[7 empty] | Capital Charges |  | 27 | 22.8 | 20 | 26.2 | 17.7
[7 empty] | Total First Year COE |  | 127.6 | 119.9 | 65.4 | 74.3 | 60.3

## Scenario 5 (Case 1-6)
Scenario 5 Calculations
Calculations | [Yellow-highlight cells are carried to data summary] |  |  |  |  | References
[7 empty] | CASE | 1-1 | 1-2 | 1-3 | 1-4 | 1-5 | 1-6 | 1-7 | 1-8 | 1-9
Flow | Value | Units | Notes | Assumptions |  |  | SOFC Degradation Rate (%/1000 h) | 1.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
With CCS | [6 empty] | SOFC Overpotential (mV) | 140 | 140 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CO2 emissions | 21.2 | lb/MWhnet |  |  |  | [1] | Capacity Factor (%) | 80 | 80 | 80 | 85 | 85 | 85 | 90 | 90 | 90
CO2 emissions | 9.6162 | kg/MWhnet | Emissions per net MWh |  |  |  | Dry Syngas CH4 Content (%) | 5.8 | 5.8 | 5.8 | 5.8 | 10.8 | 24.6 | 10.8 | 10.8 | 10.8
CO2 captured | 631.4611 | kg/MWhnet | captured CO2 per net MWh |  |  |  | SOFC Stack Cost ($/kW) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 200 | 200
Gross Power Output | 658.1 | MWgross | Gross power output for 1 hour |  |  | [1] | Inverter Efficiency (%) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 98
Net Power Output | 550.2 | MWnet | Net power output for 1 hour |  |  | [1] | PERFORMANCE
Coal Flowrate | 204600 | lb/hr |  |  |  | [1] | SOFC Cell Voltage | 0.816 | 0.816 | 0.885 | 0.885 | 0.877 | 0.866 | 0.877 | 0.877 | 0.877
Coal Flowrate | 92804.9989 | kg/hr |  |  |  |  | Gross Power (MWe) | 729.9 | 729.9 | 713.8 | 713.8 | 698.2 | 658.1 | 698.2 | 698.2 | 696.7
Coal Flowrate | 168.675 | kg/MWhnet | Emissions per net MWh |  |  |  | Auxiliary Loads (MWe) | 179.9 | 179.9 | 163.7 | 163.7 | 148 | 107.9 | 148 | 148 | 146.6
Natural Gas Flowrate | 54326 | lb/hr |  |  |  | [1] | Net Power (MWe) | 550 | 550 | 550.1 | 550.1 | 550.2 | 550.2 | 550.2 | 550.2 | 550.1
Natural Gas Flowrate | 24641.8591 | kg/hr |  |  |  |  | Coal Flowrate (lb/hr) | 406900 | 406900 | 378000 | 378000 | 352250 | 204600 | 352250 | 352250 | 348675
Natural Gas Flowrate | 44.7871 | kg/MWhnet | Emissions per net MWh |  |  |  | NG Flowrate (lb/hr) | - | - | - | - | - | 54326 | - | - | -
Raw water withdrawal | 1584 | gpm |  |  |  | [1] | Net Electric Efficiency, HHV (%) | 39.5 | 39.5 | 42.6 | 42.6 | 45.7 | 51.9 | 45.7 | 45.7 | 46.1
Raw water withdrawal | 172.7372 | gal/MWhnet |  |  |  |  | Net Plant Heat Rate, HHV (Btu/kWh) | 8630 | 8630 | 8017 | 8017 | 7468 | 6569 | 7468 | 7468 | 7394
Raw water withdrawal | 653.8814 | L/MWhnet | Consumption per net MWh |  |  |  | CO2 Capture rate (%) | 98.6 | 98.6 | 98.6 | 98.6 | 98.6 | 98.5 | 98.6 | 98.6 | 98.6
Raw water discharge | 463 | gpm |  |  |  | [1] | CO2 Emissions (lb/MWhgross) | 23.6 | 23.6 | 21.5 | 21.5 | 20.1 | 17.8 | 20.1 | 20.1 | 19.9
Raw water discharge | 50.4907 | gal/MWhnet |  |  |  |  | CO2 Emissions (lb/MWhnet) | 31.3 | 31.3 | 27.9 | 27.9 | 25.5 | 21.2 | 25.5 | 25.5 | 25.3
Raw water discharge | 191.1282 | L/MWhnet |  |  |  |  | Raw Water Consumption (gpm/MWnet) | 2.3 | 2.3 | 2 | 2 | 2.7 | 2 | 2.7 | 2.7 | 2
slag | 7673 | kg/hr |  |  |  | [1] | COST
slag | 13.9458 | kg/MWhnet |  |  |  |  | Total Plant Cost (TPC) (1000$) | 1620361 | 1620361 | 1531544 | 1531544 | 1450569 | 1166265 | 1450569 | 1435438 | 1426949
[7 empty] | Total Overnight Cost (TOC) (1000$) | 1997000 | 1997000 | 1887644 | 1887524 | 1787666 | 1432881 | 1787561 | 1769373 | 1758854
Fuel cell life | [6 empty] | Total As-Spent Cost (TASC) (1000$) | 2276579 | 2276579 | 2151914 | 2151777 | 2037939 | 1633485 | 2037820 | 2017085 | 2005093
Capacity factor | 85 | % |  |  |  | [1] | Cost of Electricity ($/MWh)
Operation hours per year | 7451.1 | hrs/yr |  |  |  |  | Variable COE | 83.8 | 37.4 | 35.5 | 34.9 | 33.2 | 37 | 32.7 | 32.3 | 32
% Fuel cell degradation per year | 1.4902 | %/yr |  |  |  |  | Fuel | 25.4 | 25.4 | 23.6 | 23.6 | 22 | 26.4 | 22 | 22 | 21.7
Percent acceptable degradation | 10 | % |  |  |  |  | Variable O&M | 58.4 | 12 | 11.9 | 11.3 | 11.2 | 10.6 | 10.7 | 10.3 | 10.3
Years of fuel cell operation | 6.7104 | yrs |  |  |  |  | Fixed O&M | 13.6 | 13.6 | 13.1 | 12.3 | 11.9 | 10.5 | 11.3 | 11.2 | 11.2
Alternative formula | 3.6364e-08 | fuel cell/MWh |  |  |  |  | Capital Charges | 64.4 | 64.4 | 60.9 | 57.3 | 54.2 | 43.5 | 51.2 | 50.7 | 50.4
number of stacks | 42 | count |  |  |  | [1] | Total First Year COE (excluding T&S) | 161.7 | 115.3 | 109.4 | 104.5 | 99.3 | 91 | 95.2 | 94.2 | 93.6
Other air emissions | [6 empty] | T&S | 8.4 | 8.4 | 7.8 | 7.8 | 7.3 | 5.5 | 7.3 | 7.3 | 7.2
SO2 | 0 | kg/MWhnet |  |  |  | [1] | Total First Year COE (including T&S) | 170.2 | 123.8 | 117.3 | 112.3 | 106.6 | 96.5 | 102.4 | 101.5 | 100.8
NOx | 0 | kg/MWhnet |  |  |  | [1] | NETL Metrics
PM | 0 | kg/MWhnet |  |  |  | [1] | % COE reduction | -21.6 | 13.3 | 17.7 | 21.4 | 25.3 | 31.6 | 28.5 | 29.2 | 29.6
HG | 0 | kg/MWhnet |  |  |  | [1] | (COEIGFC - COE IGCC with CCS)/ COEIGCC with CCS | -21.6 | 13.3 | 17.7 | 21.4 | 25.3 | 31.6 | 28.5 | 29.2 | 29.6
[7 empty] | Cost of Captured CO2 ($/tonne CO2) | 113 | 52.5 | 48.2 | 41.2 | 36.5 | 31.7 | 30.2 | 28.8 | 28.2
[7 empty] | (COEIGFC - COEAUSC PC)/ CO2 Captured (tonnes/MWh) | 113 | 52.5 | 48.2 | 41.2 | 36.5 | 31.7 | 30.2 | 28.8 | 28.2

## Conversions
Conversions
Conversion Factors |  |  |  | References
1 | kg | 2.2046 | lbm
1 | hr | 60 | minutes
1 | l | 0.26417 | gal
1 | yr | 8766 | hrs
1 | MW | 1000 | kW

## Assumptions
Assumptions
Assumption # | Description
1 | Assume a linear degradation model - a conservative estimate. The reference reports also use a first-order non-linear model that provides an upper bound to fuel cell life.

## Chart
Process
Upstream Emissions Data
Key
Electricity [Energy]
Carbon dioxide [Intermediate]
Waste (solid) [Waste for disposal]
Illinois 6 Coal [Intermediate]
Solid Oxide Fuel Cells [Intermediate]
SOFC NG and Coal plant with CCUS: System Boundary
Coal integrated gasification solid oxide fuel cell (SOFC) and natural gas (NG) solid fuel cell power plants with and without carbon capture.
Natural Gas [Intermediate]