## Info
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
DS Sheet Information
|  | Process Name: | Operation of NETL Baseline SubCPC Power Plant
|  | Process Description: | The operations of the NETL baseline Subcritical Pulverized Coal (SubCPC) power plants with or without carbon capture and sequestration (CCS) on the basis of 1 MWh electricity output.
|  | Files: | This unit process is composed of this document and the file, DF_Stage3_O_SubCPC_Power_Plant_Baseline_2015.01.docx, which provides additional details regarding calculations, data quality, and references as relevant.
|  | Summary and Calculations Worksheets: | As shown below, this document contains 3 summary worksheets (Data Summary, Reference Source Info, and DQI) that have been formatted consistent with NETL standards. The remaining 'calculations' worksheets are workspaces used by NETL engineers during the production of this unit process. The 'calculations' worksheets are presented for the convenience of the reader, and have not been subjected to standardized formatting.
This data sheet is organized as follows:
|  | Worksheet | Description
| Summary | Data Summary | Summary of Calculations, Input and Output Flows, Reference Flow, and other information
|  | Parameter Scenarios | Parameters for various scenarios where the unit process is used
|  | Reference Source Info | Referenced citations; citations are referenced by number, listed at the top of the Reference Source Info sheet
|  | DQI | Data Quality Index
| Calculations | Baseline | Baseline emissions data
|  | Consump & Waste | Materials consumed and wastes produced
|  | Aux Boiler | Natural gas use in auxiliary boiler
|  | Conversions | Unit Conversions
|  | Assumptions | Assumptions
|  | GaBi Import | Data Summary page formatted for importation into the GaBi 4.4 software
How to Cite This Document:
This document should be cited as: NETL (2015). NETL Life Cycle Inventory Data – Unit Process: Operation of NETL Baseline SubCPC Power Plant - Version 01. U.S. Department of Energy, National Energy Technology Laboratory. Retrieved [DATE] from http://www.netl.doe.gov/LCA
Additional Notes:
|  | For the calculations sheets, values |  | highlighted in yellow | are also pulled forward into the 'Data Summary' sheet
Bibliographic references & assumptions referenced by number; see 'Reference Source Info' & 'Assumptions' sheets for cross-reference.
Data Summary sheet color coding: white indicates data input by model engineer; blue indicates automatically calculated values
Abbreviations used throughout this DS: Subrcritical Pulverized Coal (SubCPC)
Selective catalytic reduction (SCR)
Disclaimer:
Template Version:
1.0
Neither the U.S. Department of Energy (DOE) National Energy Technology Laboratory (NETL) nor any person acting on behalf of these organizations:
A. Makes any warranty or representation, express or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that the use of any information, apparatus, method, or process disclosed in this document may not infringe on privately owned rights; or
B. Assumes any liability with this report as to its use, or damages resulting from the use of any information, apparatus, method, or process disclosed in this document.
Reference herein to any specific commercial product, process, or service by trade name, trademark, manufacturer, or otherwise, does not necessarily constitute or imply its endorsement, recommendation, or favoring by NETL. The views and opinions of the authors expressed herein do not necessarily state or reflect those of NETL.

## Data Summary
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
Data Module Summary
Process Name: |  | Operation of NETL Baseline SubCPC Power Plant
Reference Flow: |  | 1 | MWh | of | Electricity | [5 empty] | DQI | 3,3,3,1,2 | (see DQI sheet for explanation)
Brief Description: |  | The operations of the NETL baseline Subcritical Pulverized Coal (SubCPC) power plants with or without carbon capture and sequestration (CCS) on the basis of 1 MWh electricity output.
SECTION I: META DATA
Geographical Coverage: |  | USA |  |  | Goal and Scope:
Region |  | Midwest |  |  | Reference Flow: 1 MWh of Electricity
Year Data Best Represents: |  | 2015
Process Type: |  | Energy Conversion (EC) |  |  | This unit process provides a summary of relevant input and output flows associated with the production of electricity by the combustion of coal in the subcritical pulverized coal power plants defined in the NETL baseline studies. This process can be used for scenarios with and without CCS. Key inputs include Illinois No. 6 coal and water from ground and municipal sources and combustion of natural gas in an auxiliary boiler. Key outputs include electricity, greenhouse gas emissions to air, and waste water.
Process Scope: |  | Gate-to-Gate Process (GG)
Allocation Applied: |  | No
Completeness: |  | Individual Relevant Flows Captured
Flows Aggregated in Data Set: |  |  |  |  | Note: All inputs and outputs are normalized per the reference flow (e.g., per MWh of electricity)
SECTION II: PARAMETERS
This section includes adjustable parameters, calculations needed to support adjustable parameters, and flow calculations based upon adjustable parameters.
| Parameter Name | Formula | Value | Min. Value | Max. Value | Unit | References | Comments
2 | CF |  | 0.85 |  |  |  | 1 | [dimensionless] Capacity Factor of SubCPC plant
3 | CCS |  | 0 |  |  |  |  | [binary] If CO2 in flue gas is routed to CO2 recovery, value = 1. If CO2 in flue gas is released to atmosphere, value = 0.
12 | Net_MW_noCCS |  | 550 |  |  | MWh | 1 | [MWh] Net Power Output for a single hour of SubCPC without CCS operation
10 | Net_MW_CCS |  | 550 |  |  | MWh | 1 | [MWh] Net Power Output for a single hour of SubCPC with CCS operation
6 | Net_MW | IF(CCS=1;Net_MW_CCS;Net_MW_noCCS) | 550 |  |  | MWh |  | [MWh] Net Power Output for a single hour of SubCPC operation with or without CCS, depending on value of "CCS" parameter
9 | Life_time |  | 30 |  |  | yrs |  | [Years] Life time of a power plant
6 | Plants | 1/(Life_time*365.25*24*Net_MW*CF) | 8.1338e-09 |  |  | pce/MWh |  | [Piece/MWh] Fraction of a power plant per MWH
14 | Sub_CO2caprate |  | 0.9 |  |  |  | 1 | [dimensionless] Fraction of CO2 captured
11 | Sub_CO2_CCS |  | 101.1511 |  |  | kg/MWh | 1 | [kg/MWh] CO₂ emissions to air per MWh with CCS
13 | Sub_CO2_noCCS |  | 806.9408 |  |  | kg/MWh | 1 | [kg/MWh] CO₂ emissions to air per MWh without CCS
7 | Sub_CO2 | IF(CCS=1;sub_CO2_CCS;sub_CO2_noCCS) | 806.9408 |  |  | kg/MWh |  | [kg/MWh] CO₂ emissions to air per MWh without or without CCS, depending on value of "CCS" parameter
11 | Sub_CO2_cap | IF(CCS=1;(Sub_CO2*Sub_CO2caprate/(1-Sub_CO2caprate); 0) | 0 |  |  | kg/MWh |  | [kg/MWh] CO₂ captured for CCS
11 | Sub_NOx_CCS |  | 0.37178 |  |  | kg/MWh | 1 | [kg/MWh] NOx emissions to air per MWh with CCS
13 | Sub_NOx_noCCS |  | 0.33541 |  |  | kg/MWh | 1 | [kg/MWh] NOx emissions to air per MWh without CCS
7 | Sub_NOx | IF(CCS=1;Sub_NOx_CCS;Sub_NOx_noCCS) | 0.33541 |  |  | kg/MWh |  | [kg/MWh] NOx emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
11 | Sub_SO2_CCS |  | 0 |  |  | kg/MWh | 1 | [kg/MWh] SO₂ emissions to air per MWh with CCS
13 | Sub_SO2_noCCS |  | 0.33541 |  |  | kg/MWh |  | [kg/MWh] SO₂ emissions to air per MWh without CCS
7 | Sub_SO2 | IF(CCS=1;Sub_SO2_CCS;Sub_SO2_noCCS) | 0.33541 |  |  | kg/MWh |  | [kg/MWh] SO₂ emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
10 | Sub_PM_CCS |  | 0.0478 |  |  | kg/MWh | 1 | [kg/MWh] PM emissions to air per MWh with CCS
12 | Sub_PM_noCCS |  | 0.043124 |  |  | kg/MWh |  | [kg/MWh] PM emissions to air per MWh without CCS
6 | Sub_PM | IF(CCS=1;Sub_PM_CCS;Sub_PM_noCCS) | 0.043124 |  |  | kg/MWh |  | [kg/MWh] PM emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
10 | Sub_Hg_CCS |  | 1.5933e-06 |  |  | kg/MWh | 1 | [kg/MWh] Hg emissions to air per MWh with CCS
12 | Sub_Hg_noCCS |  | 1.4375e-06 |  |  | kg/MWh |  | [kg/MWh] Hg emissions to air per MWh without CCS
6 | Sub_Hg | IF(CCS=1;Sub_Hg_CCS;Sub_Hg_noCCS) | 1.4375e-06 |  |  | kg/MWh |  | [kg/MWh] Hg emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | Sub_coal_CCS |  | 425.6923 |  |  | kg/MWh | 1 | [kg/MWh] Coal consumption per MWh with CCS
14 | Sub_coal_noCCS |  | 339.786 |  |  | kg/MWh | 1 | [kg/MWh] Coal consumption per MWh without CCS
8 | Sub_coal | IF(CCS=1;Sub_coal_CCS;Sub_coal_noCCS) | 339.786 |  |  | kg/MWh |  | [kg/MWh] Coal consumption per MWh with or without CCS, depending on value of "CCS" parameter
12 | Sub_H2OinCCS |  | 3485.7448 |  |  | L/MWh | 1 | [L/MWh] Water withdrawal with CCS
14 | Sub_H2OinnoCCS |  | 2286.9393 |  |  | L/MWh | 1 | [L/MWh] Water withdrawal without CCS
9 | Sub_H2Oin | IF(CCS=1;Sub_H2OinCCS;Sub_H2OinnoCCS) | 2286.9393 |  |  | L/MWh |  | [L/MWh] Water withdrawal with or without CCS, depending on value of "CCS" parameter
12 | Sub_H2OinGnd | Sub_H2Oin/2 | 1143.4697 |  |  | L/MWh | 1 | [L/MWh] Ground water withdrawal
12 | Sub_H2OinMun | Sub_H2Oin/2 | 1143.4697 |  |  | L/MWh | 1 | [L/MWh] Municipal water withdrawal
13 | Sub_H2OoutCCS |  | 792.8717 |  |  | L/MWh | 1 | [L/MWh] Waste water with CCS
14 | Sub_H2OoutnCCS |  | 469.5287 |  |  | L/MWh | 1 | [L/MWh] Waste water without CCS
10 | Sub_H2Oout | IF(CCS=1;Sub_H2OoutCCS;Sub_H2OoutnCCS) | 469.5287 |  |  | L/MWh |  | [L/Mwh] Waster water with or without CCS, depending on value of "CCS"Parameter
7 | CF_AuxB |  | 0.5 |  |  |  | 1 | [Dimensionless] Fraction of downtime that auxliary boiler operates
15 | AuxB_opt_factor | (1-CF)*CF_AuxB | 0.075 |  |  |  | 1 | [Dimensionless] Fraction of total time that auxiliary boiler operates
14 | NG_AuxB_tot_kg |  | 1010.1009 |  |  | kg/hr | 3 | [kg/hr] Natural gas consumption for auxiliary boiler
7 | NG_AuxB | (AuxB_opt_factor*NG_AuxB_tot_kg)/(Net_MW*CF) | 0.16205 |  |  | kg/MWh |  | [kg/MWh] Natural gas consumption in auxiliary boiler
12 | act_carb_CCS |  | 0.2749 |  |  | kg/MWh | 1 | [kg/MWh] Activated carbon consumed for operation with CCS
14 | act_carb_noCCS |  | 0.20618 |  |  | kg/MWh | 1 | [kg/MWh] Activated carbon consumed for operation without CCS
8 | act_carb | IF(CCS=1;act_carb_CCS;act_carb_noCCS) | 0.20618 |  |  | kg/MWh |  | [kg/MWh] Activated carbon consumed for operation
13 | limestone_CCS |  | 55.8056 |  |  | kg/MWh | 1 | [kg/MWh] Limestone consumed for operation with CCS
15 | limestone_noCCS |  | 33.6071 |  |  | kg/MWh | 1 | [kg/MWh] Limestone consumed for operation without CCS
9 | limestone | IF(CCS=1;limestone_CCS;limestone_noCCS) | 33.6071 |  |  | kg/MWh |  | [kg/MWh] Limestone consumed for operation
8 | lime_CCS |  | 8.5908 |  |  | kg/MWh | 1 | [kg/MWh] Hydrated lime consumed for operation with CCS
10 | lime_noCCS |  | 6.8726 |  |  | kg/MWh | 1 | [kg/MWh] Hydrated lime consumed for operation without CCS
4 | lime | IF(CCS=1;lime_CCS;lime_noCCS) | 6.8726 |  |  | kg/MWh |  | [kg/MWh] Hydrated lime consumed for operation
14 | NH3_consum_CCS |  | 6.3228 |  |  | kg/MWh | 1 | [kg/MWh] Ammonia consumed for operation with CCS
15 | NH3_consum_nCCS |  | 4.9483 |  |  | kg/MWh |  | [kg/MWh] Ammonia consumed for operation without CCS
10 | NH3_consum | IF(CCS=1;NH3_consum_CCS;NH3_consum_nCCS) | 4.9483 |  |  | kg/MWh |  | [kg/MWh] Ammonia consumed for operation
11 | SCR_cat_CCS |  | 0.031061 |  |  | L/MWh | 1 | [L/MWh] SCR catalyst required for operation with CCS
13 | SCR_cat_noCCS |  | 0.025 |  |  | L/MWh | 1 | [L/MWh] SCR catalyst required for operation without CCS
7 | SCR_cat | IF(CCS=1;SCR_cat_CCS;SCR_cat_noCCS) | 0.025 |  |  | L/MWh |  | [L/MWh] SCR catalyst required for operation
15 | trieth_glyc_CCS |  | 0.11672 |  |  | L/MWh | 1 | [L/MWh] Triethylene glycol required for CCS
11 | trieth_glyc | If(CCS=1;trieth_glyc_CCS;0) | 0 |  |  | L/MWh |  | [L/MWh] Triethylene glycol required for CCS
14 | water_chem_CCS |  | 1.0109 |  |  | kg/MWh | 1 | [kg/MWh] Makeup water chemical demand with CCS
15 | water_chem_nCCS |  | 0.66321 |  |  | kg/MWh | 1 | [kg/MWh] Makeup water chemical demand without CCS
10 | water_chem | IF(CCS=1;water_chem_CCS;water_chem_nCCS) | 0.66321 |  |  | kg/MWh |  | [kg/MWh] Makeup water chemical demand
14 | unsp_Waste_CCS |  | 4.7421 |  |  | kg/MWh | 1 | [kg/MWh] Unspecified type waste produced for disposal with CCS
10 | unsp_Waste | IF(CCS=1;Waste_CCS;0) | 0 |  |  | kg/MWh |  | [kg/MWh] Unspecified type waste produced for disposal
13 | sol_waste_CCS |  | 50.5137 |  |  | kg/MWh | 1 | [kg/MWh] Solid waste produced for disposal with CCS
15 | sol_waste_noCCS |  | 40.2735 |  |  | kg/MWh | 1 | [kg/MWh] Solid waste produced for disposal without CCS
9 | sol_waste | IF(CCS=1;sol_waste_CCS;sol_waste_noCCS) | 40.2735 |  |  | kg/MWh |  | [kg/MWh] Solid waste produced for disposal
10 | gypsum_CCS |  | 7.285 |  |  | kg/MWh | 1 | [kg/MWh] Gypsum produced as byproduct with CCS
12 | gypsum_noCCS |  | 5.773 |  |  | kg/MWh | 1 | [kg/MWh] Gypsum produced as byproduct without CCS
6 | gypsum | IF(CCS=1;sol_waste_CCS;sol_waste_noCCS) | 5.773 |  |  | kg/MWh |  | [kg/MWh] Gypsum produced as byproduct
| End of List | <select this entire row, then insert new row>
SECTION III: INPUT FLOWS
This section includes all input flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
| Plants | SubCPC power plant [Construction] | 1 | kg | 8.1338e-09 | pce/MWh | 8.1338e-09 | kg | X |  | 1 | [Technosphere] SubCPC power plant
| Sub_coal | Hard Coal (Illinois No 6) [Hard coal (resource)] | 1 | kg | 339.786 | kg/MWh | 339.786 | kg | X |  | 1 | [Technosphere] Coal for combustion
| NG_AuxB | Natural gas combustion in auxiliary boiler | 1 | kg | 0.16205 | kg/MWh | 0.16205 | kg | X |  | 1,3 | [Technosphere] Natural gas combusted in auxiliary boiler
| Sub_H2OinGnd | Water (ground water) [Water] | 1 | L | 1143.4697 | L/MWh | 1143.4697 | L |  |  | 1 | [Resource] Ground water withdrawal
| Sub_H2OinMun | Water (municipal) [Water] | 1 | L | 1143.4697 | L/MWh | 1143.4697 | L | X |  | 1 | [Technosphere] Municipal water withdrawal
| act_carb | Activated carbon | 1 | kg | 0.20618 | kg/MWh | 0.20618 | kg | X |  | 1 | [Technosphere] Activated carbon consumption
| limestone | Limestone | 1 | kg | 33.6071 | kg/MWh | 33.6071 | kg | X |  | 1 | [Technosphere] limestone for treatment consumption
| lime | Hydrated Lime | 1 | kg | 6.8726 | kg/MWh | 6.8726 | kg | X |  | 1 | [Technosphere] Hydrated lime consumption
| NH3_consum | Ammonia [Material] | 1 | kg | 4.9483 | kg/MWh | 4.9483 | kg | X |  | 1 | [Technosphere] Ammonia consumption
| SCR_cat | SCR catalyst [Material] | 1 | L | 0.025 | L/MWh | 0.025 | L | X |  | 1 | [Technosphere] SCR catalyst consumption
| trieth_glyc | Triethylene glycol [Material] | 1 | L | 0 | L/MWh | 0 | L | X |  | 1 | [Technosphere] Triethylene glycol consumption
| water_chem | Makeup water treatment chemicals [Material] | 1 | kg | 0.66321 | kg/MWh | 0.66321 | kg | X |  | 1 | [Technosphere] Makeup water treatment chemicals
| End of List | <select this entire row, then insert new row> | Factor |  |  |  | Amount |  |  | <select from list>
SECTION IV: OUTPUT FLOWS
This section includes all output flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
|  | Power [Electric Power] | 1 | MWh | 1 |  | 1 |  | X |  |  | Reference flow
| gypsum | Gypsum | 1 | kg | 5.773 | kg/MWh | 5.773 | kg | X |  | 1 | By-product
| Sub_CO2_cap | Carbon dioxide [Inorganic intermediate products] | 1 | kg | 0 | kg/MWh | 0 | kg | X |  | 1 | CO₂ captured for CCS
| Sub_CO2 | Carbon dioxide [Inorganic emissions to air] | 1 | kg | 806.9408 | kg/MWh | 806.9408 | kg |  |  | 1 | Emission to air
| Sub_NOx | Nitrogen oxides [Inorganic emissions to air] | 1 | kg | 0.33541 | kg/MWh | 0.33541 | kg |  |  | 1 | Emission to air
| Sub_SO2 | Sulphur dioxide [Inorganic emissions to air] | 1 | kg | 0.33541 | kg/MWh | 0.33541 | kg |  |  | 1 | Emission to air
| Sub_PM | Dust (unspecified) [Particles to air] | 1 | kg | 0.043124 | kg/MWh | 0.043124 | kg |  |  | 1 | Emission to air
| Sub_Hg | Mercury (+II) [Heavy metals to air] | 1 | kg | 1.4375e-06 | kg/MWh | 1.4375e-06 | kg |  |  | 1 | Emission to air
| Sub_H2Oout | Water (wastewater) [Water] | 1 | L | 469.5287 | L/MWh | 469.5287 | L |  |  | 1 | Renewable resources
| unsp_Waste | Waste (unspecified) | 1 | kg | 0 | kg/MWh | 0 | kg | * |  | 1 | Waste
| sol_waste | Waste [Solid Waste] | 1 | kg | 40.2735 | kg/MWh | 40.2735 | kg | * |  | 1 | Solid Waste
| End of List | <select this entire row, then insert new row> | Factor | [6 empty] | <select from list>
Detailed Spreadsheet Lists
| Process Type | Process Scope | Completeness |  |  | Origin |  | Tracked
| <select from list> | <select from list> | <select from list> |  |  | <select from list>
| Extraction Process (EP) | Cradle-to-Grave (End-of-Life) Process (CE) | All Flows Captured |  |  | Measured |  | X
| Manufacturing Process (MP) | Cradle-to-Gate Process (CG) | All Relevant Flows Captured |  |  | Calculated |  | *
| Installation Process (IP) | Gate-to-Gate Process (GG) | Individual Relevant Flows Captured |  |  | Literature
| Basic Process (BP) | Gate-to-Grave (End-of-Life) Process (GE) | Some Relevant Flows Not Captured |  |  | Estimated
| Energy Conversion (EC) |  | No Statement |  |  | No Statement
Transport Process (TP)
Recovery Process (RP)
Waste Treatment Process (WT)
Auxiliary Process (AP)
Process
Energy Use
Energy P&D
Material P&D

## Reference Source Info
Field Name
Number | 1 | 2 | 3
SourceType | Separate Publication | Separate Publication | Separate Publication
Title | Cost and Performance Baseline for Fossil Energy Plants Volume 1a: Bituminous Coal (PC) and Natural Gas to Electricity Revision 3 | Toxic Releases Inventory | 40000 PPH Nebraska, Watertube, trailer mounted, 350 psi, gas/oil (3)
FirstAuthor | NETL | EPA | Wabash Power Equipment Co
AdditionalAuthors | Tim Fout, Alexander Zoelle, Dale Keairns, Lora Pinkerton, Marc Turner, Mark Woods, Norma Kuehn, Vasant Shah, Vincent Chou
Year | 2015 | 2012 | 2008
Date
PlaceOfPublication | Pittsburgh, PA |  | Wheeling, IL
Publisher | DOE, National Energy Technology Laboratory | EPA
PageNumbers
Table or Figure Number
NameOfEditors
TitleOfAnthology
Journal
VolumeNo
IssueNo
Docket Number
Copyright
Internet Address |  | http://www.epa.gov/enviro/facts/tri/search.html
Internet Access Date |  | August 14, 2012
Data Type (Origin) | Literature | Database | Literature
Year Data Represents |  | 2006-2011 | Estimated 1999
Geographical Representation | USA | USA
Representativeness | Average industry | Specific site data | Product Representative from Brochure
BibliographicText | NETL, 2015. Cost and Performance Baseline for Fossil Energy Plants Volume 1a: Bituminous Coal (PC) and Natural Gas to Electricity Revision 3, DOE, National Energy Technology Laboratory, Pittsburgh, PA. Accessed on at . | EPA, 2012. Toxic Releases Inventory, EPA, . Accessed on August 14, 2012 at http://www.epa.gov/enviro/facts/tri/search.html. | Wabash Power Equipment Co, 2008. 40000 PPH Nebraska, Watertube, trailer mounted, 350 psi, gas/oil (3), , Wheeling, IL. Accessed on at .
Text/Description | Specifications and analysis results from baseline SubCPC plants. | Lead emissions for 6 coal power plants
Reference Source Info Lists
Source Type
<select from list>
Undefined
Article
Chapters in Anthology
Separate Publication
Measurement on Site
Oral Communication
Personal Written Communication
Questionnaires

## DQI
Data Quality Index
DQI Determination
| Input/Output | Reference (see 'Reference Source Info' worksheet) | Source Reliability | Completeness | Temporal Correlation | Geographical Correlation | Technical Correlation | DQI | Recommendations | Determinations
| Aux boiler natural gas | 1,3 | 2 | N/A | 3 | 1 | 2 | 2,N/A,3,1,2 | Requirements met | OK
| All other flows | 1 | 3 | 3 | 1 | 1 | 1 | 3,3,1,1,1 | Requirements met | OK
| Total | [6 empty] | 3,3,3,1,2
DQI Methodology
DQI Matrix (from NETL LCI&C Guideline Document, adapted from Weidema and Wenaes)
| Indicator | Score
|  | 1 | 2 | 3 | 4 | 5
| Source Reliability (for most applications, source quality guidelines only factor) | data verified based on measurements | data verified based on some assumptions and/or standard science and engineering calculations | data verified with many assumptions, or non-verified but from quality source | qualified estimate | non-qualified estimate
|  | source quality guidelines met |  | source quality guidelines not met
|  | data cross checks, greater than or equal to 3 quality sources | 2 or less data sources available for cross check, or data sources available that do not meet quality standards |  | no data available for cross check
| Completeness | representative data from a sufficient sample of sites over an adequate period of time | smaller number of site but an adequate period of time | sufficient number of sites but a less adequate period of time | smaller number of sites and shorter periods or incomplete data from an adequate number of sites or periods | representativeness unknown or incomplete data sets
| Temporal Correlation | less than three years of difference to year of study/current year | less than 6 years of difference | less than 10 years difference | less than 15 years difference | age of data unknown or more than 15 years difference
| Geographical Correlation | data from area under study | average data from larger area or specific data from a close area | data from area with similar production conditions | data from area with slightly similar production conditions | data from unknown area or area with very different production conditions
| Technological Correlation | data from technology, process or materials being studied | data from a different technology using the same process and/or materials |  | data on related process or material using the same technology | data or related process or material using a different technology
Indicator Descriptions
Source Reliability -- This indicator relates to the quality of the data source and the verification of the data collection methods used within the source.
Data Verification -- Source data that have been verified within error bounds by either the source author (with a high level of transparency) or the LCI modeler. Verification can be done by measurement, including on-site checking, recalculation, or mass or energy balance analysis. If the source data cannot be verified without making assumptions (i.e., not enough data are available to close the mass/energy balance), then the score should be a 2 or 3, depending on the number of assumptions. If no source data are available, a qualified estimate from an expert in the field should receive a score of 4, and an estimate from a non-expert should receive a score of 5. Mostly applicable to primary data.
Source Quality Guidelines -- The highest quality source should be
o From a peer reviewed journal or a government sponsored study. If the source is an LCA, it must meet ISO requirements.
o Publicly available either for free or at cost, or directly representative of the process of interest.
o Written/published by an unbiased party.
o An unbiased survey of experts or process locations.
When the source used for data is a reputable model that does not specifically meet the above criteria, it is the discretion of the modeler to determine the rank of the source. An example for justification would be if the data have been used in published reports that met the data quality standards.
Data Cross-Check -- The number of sources that verify the same data point or series, within reason. As a general benchmark, a high standard is greater than or equal to three data cross checks with quality approved sources. This typically refers to primary data, and if no other data sources are available, this can be omitted.
Completeness -- This indicator quantifies the statistical robustness of the source data. This ranking is based on how many data points were taken, how representative the sample is to the studied process, and whether the data were taken for an acceptable time period to even out normal process fluctuations. The following examples are given to help clarify this indicator.
Temporal Correlation -- This indicator represents how well the time period in which the data were collected corresponds with the year of the study. If the study is set to evaluate the use of a technology from 2000 to 2040, data from 1970 would not be very accurate. It is important when assigning this ranking to take notice of any discrepancies between the year the source was published and the year(s) the data were collected.
Geographical Correlation -- This indicator represents the appropriateness between the region of study and the source data region. This indicator becomes important when comparing data from different countries. For example, technological advances might reasonably be expected to develop differently in different countries, so efficiency and energy use might be very different. This is also important when looking at best management practices for carbon mitigation.
Technological Correlation -- This indicator embodies all other differences that may be present between the study goals and the data source. From the above example, using data for a type of biomass that is not being studied in the LCA should result in a lower technological representativeness ranking.
Steps for Applying DQM
1) Calculate score for each unit process (UP) input. If more than one reference source is used for one input, and the score is lower, consider both scores. If an indicator does not relate to a specific source, assume N/A. If all emissions come from one source, only one score is needed
- when a score is determined for a particular reference source, add to 'Reference Source Info' for future use
2) From the reference scores, determine the data quality indicator (DQI) for the unit process inputs for commissioning/decommissioning operations (when applicable)*
- the scores are not additive, rather, the lowest score for an indicator of a particular data input is the lowest score for the UP
3) Significant inputs of low quality unit processes (DQI mostly 3-5) should be varied to the minimum and maximum values or 95 percent confidence interval of the uncertainty range.
- check significance first. If the input is not significant by a long shot (or with the maximum possible value), it is not necessary to include in the UP
4) If the change in the final result from a single unit process is greater than a threshold value, for example, 0.1 g CO2e/MJ, then the processes should be flagged for possible additional data quality refinement
- for example, if emissions from the total steel inputs are found to be significant during sensitivity, the DQI will be performed on the steel profile. If this is not possible (because data are not transparent/purchased), it will be listed as a future recommendation
- if, however, the steel inputs are significant due to a large amount of steel needed for a particular process, then the DQI on that input should be performed and the data refined if needed
5) If the UP input is significant (with or without sensitivity), but no data refinement is possible, this is listed as a data limitation and noted in the report
* For NETL LCI&C studies, because data quality for construction is typically low, sensitivity on those inputs is already performed and the DQI does not need to be calculated. If sensitivity is not performed on construction, or sensitivity shows that a particular input is significant, then the DQI will be performed

## Baseline
Baseline
Calculations | [5 empty] | References
Emissions w/o CCS
Flow | Value | Units | Notes | Assumptions
CO2 | 1779 | lb/MWhnet |  |  |  | [1]
CO2 | 806.9408 | kg/MWhnet | Emissions per net MWh
Gross Power Output | 581 | MWhgross | Gross power output for 1 hour |  |  | [1]
Net Power Output | 550 | MWhnet | Net power output for 1 hour |  |  | [1]
NOx | 0.7 | lb/MWhgross |  |  |  | [1]
NOx | 0.31751 | kg/MWhgross
NOx | 0.33541 | kg/MWhnet | Emissions per net MWh
SO2 | 0.7 | lb/MWhgross |  |  |  | [1]
SO2 | 0.31751 | kg/MWhgross
SO2 | 0.33541 | kg/MWhnet
PM | 0.09 | lb/MWhgross |  |  |  | [1]
PM | 0.040823 | kg/MWhgross
PM | 0.043124 | kg/MWhnet
Hg | 3e-06 | lb/MWhgross |  |  |  | [1]
Hg | 1.3608e-06 | kg/MWhgross
Hg | 1.4375e-06 | kg/MWhnet
Coal Flowrate | 412005 | lb/hr |  |  |  | [1]
Coal Flowrate | 186882.3244 | kg/hr
Coal Flowrate | 339.786 | kg/MWhnet
Raw water withdrawal | 5538 | gpm |  |  |  | [1]
Raw water withdrawal | 604.1455 | gal/MWh
Raw water withdrawal | 2286.9393 | L/MWhnet
Water discharge | 1137 | gpm |  |  |  | [1]
Water discharge | 124.0364 | gal/MWhnet
Water discharge | 469.5287 | L/MWhnet
Emissions w/ CCS
CO2 | 223 | lb/MWhnet |  |  |  | [1]
CO2 | 101.1511 | kg/MWhnet | Emissions per net MWh
Gross Power Output | 644 | MWhgross | Gross power output for 1 hour |  |  | [1]
Net Power Output | 550 | MWhnet | Net power output for 1 hour |  |  | [1]
NOx | 0.7 | lb/MWhgross |  |  |  | [1]
NOx | 0.31751 | kg/MWhgross
NOx | 0.37178 | kg/MWhnet | Emissions per net MWh
SO2 | 0 | lb/MWhgross |  |  |  | [1]
SO2 | 0 | kg/MWhgross
SO2 | 0 | kg/MWhnet
PM | 0.09 | lb/MWhgross |  |  |  | [1]
PM | 0.040823 | kg/MWhgross
PM | 0.0478 | kg/MWhnet
Hg | 3e-06 | lb/MWhgross |  |  |  | [1]
Hg | 1.3608e-06 | kg/MWhgross
Hg | 1.5933e-06 | kg/MWhnet
Coal Flowrate | 516170 | lb/hr |  |  |  | [1]
Coal Flowrate | 234130.7736 | kg/hr
Coal Flowrate | 425.6923 | kg/MWhnet
Raw water withdrawal | 8441 | gpm |  |  |  | [1]
Raw water withdrawal | 920.8364 | gal/MWhnet
Raw water withdrawal | 3485.7448 | L/MWhnet
Water discharge | 1920 | gpm/MWnet |  |  |  | [1]
Water discharge | 209.4545 | gal
Water discharge | 792.8717 | L/MWhnet

## Consump & Waste
NGCC Baseline Cases
Calculations | [5 empty] | References
Consumption w/out CCS
Flow | Value | Units | Notes | Assumptions
Net Power | 550 | MW |  |  |  | [1]
Daily Generation | 13200 | MWh/day
Makeup and Waste Water Treamtent Chemicals | 19300 | lb/day |  |  |  | [1]
| 8754.3327 | kg/day
| 0.66321 | kg/MWh
SCR Catalyst | 0.33 | m3/day |  |  |  | [1]
| 330 | l/day
| 0.025 | l/MWh
Ammonia | 72 | ton/day |  |  |  | [1]
| 65317.3013 | kg/day
| 4.9483 | kg/MWh
Limestone | 489 | ton/day |  |  |  | [1]
| 443613.3379 | kg/day
| 33.6071 | kg/MWh
Hydrated Lime | 100 | ton/day |  |  |  | [1]
| 90718.474 | kg/day
| 6.8726 | kg/MWh
Activated Carbon | 3 | ton/day |  |  |  | [1]
| 2721.5542 | kg/day
| 0.20618 | kg/MWh
Waste Disposal w/out CCS
Fly Ash | 490 | ton/day |  |  |  | [1]
| 444520.5226 | kg/day
| 33.6758 | kg/MWh
Bottom Ash | 96 | ton/year |  |  |  | [1]
| 87089.735 | kg/day
| 6.5977 | kg/MWh
total solid waste | 40.2735 | kg/MWh
By-Products w/out CCS
Gypsum | 84 | ton/day
| 76203.5182 | kg/yr
| 5.773 | kg/MWh
Consumption w/ CCS
Net Power | 550 | MW |  |  |  | [1]
Daily Generation | 13200 | MWh/day
Makeup and Waste Water Treamtent Chemicals | 29418 | lb/day |  |  |  | [1]
| 13343.7803 | kg/day
| 1.0109 | kg/MWh
SCR Catalyst | 0.41 | m3/day |  |  |  | [1]
| 410 | l/day
| 0.031061 | l/MWh
Triethylene Glycol | 407 | gal/day |  |  |  | [1]
| 1540.6626 | l/day
| 0.11672 | l/MWh
Ammonia | 92 | ton/day |  |  |  | [1]
| 83460.9961 | kg/day
| 6.3228 | kg/MWh
Limestone | 812 | ton/day |  |  |  | [1]
| 736634.0089 | kg/day
| 55.8056 | kg/MWh
Hydrated Lime | 125 | ton/day |  |  |  | [1]
| 113398.0925 | kg/day
| 8.5908 | kg/MWh
Activated Carbon | 4 | ton/day |  |  |  | [1]
| 3628.739 | kg/day
| 0.2749 | kg/MWh
Waste Disposal w/CCS
Amine Purification Unit Waste | 21 | ton/day |  |  |  | [1]
| 19050.8795 | kg/day
| 1.4432 | kg/MWh
Thermal Reclaimer Unit waste | 2 | ton/day |  |  |  | [1]
| 1814.3695 | kg/day
| 0.13745 | kg/MWh
Prescrubber Blowdown waste | 46 | ton/day |  |  |  | [1]
| 41730.498 | kg/day
| 3.1614 | kg/MWh
Fly Ash | 614 | ton/day |  |  |  | [1]
| 557011.4304 | kg/day
| 42.1978 | kg/MWh
Bottom Ash | 121 | ton/day |  |  |  | [1]
| 109769.3535 | kg/day
| 8.3159 | kg/MWh
total solid waste | 50.5137 | kg/MWh
total unspecified waste | 4.7421 | kg/MWh
By-Products w/ CCS
Gypsum | 106 | ton/day
| 96161.5824 | kg/day
| 7.285 | kg/MWh

## Aux Boiler
Sheet Name Here
Calculations |  |  |  | Assumptions |  | References
Auxiliary Boiler
Without CCS
Auxiliary boiler NG consumption | 53000 | SCF/hr |  | 2 |  | [3] | This consumption rate is correlated with several other internet sources: | 54,650 SCF/hr | http://www.nationwideboiler.com/pdfs/specs/equipment/40KPPH700TM_G2_LN_B420.pdf
| 2226.8908 | lb/hr
| 1010.1007 | kg/hr
Time NGCC plant up | 0.85 | yr |  |  |  | [1] Capacity factor
or | 0.85 | hr
NGCC PLant downtime | 0.15 | hr |  | 1
Fraction of downtime Aux. boiler runs | 0.5
| 0.075 | hr
Aux boiler NG consumption during downtime | 75.7575 | kg/hr
Power plant net output | 550 | MW |  |  |  | [1]
Aux boiler NG consumed per MWh | 0.16205 | kg/MWh | The power plant is able to produce 1MWh of power in a fraction of an hour (actually 0.1 minutes), so the auxiliary boiler operation is scaled accordingly and also scaled due to the fraction of an hour that the plant is operating (85%).
Aux boiler alternative calculation
Power plant life | 30 | years
| 262980 | hours
Plant operating time | 223533 | hours | 85% of 30 years
Power plant total MWh | 122943150 | MWh | 549.990 MW * operating time
Downtime | 39447 | hours | 15% of 30 years
Aux boiler time | 19723.5 | hours | 50% of downtime
Aux boiler NG consumption | 19922720.2863 | kg | 1010.10 kg/hr * boiler time
Aux boiler NG consumption/MWh | 0.16205 | kg/MWh | total boiler NG consumption/Power plant total MWh
With CCS
Auxiliary boiler NG consumption | 53000 | SCF/hr |  | 2 |  | [3]
| 2226.8908 | lb/hr
| 1010.1007 | kg/hr
Time NGCC plant up | 0.85 | yr |  |  |  | [1] Capacity factor
or | 0.85 | hr
NGCC PLant downtime | 0.15 | hr |  | 1
Fraction of downtime Aux. boiler runs | 0.5
| 0.075 | hr
Aux boiler NG consumption during downtime | 75.7575 | kg/hr
Power plant net output | 550 | MW |  |  |  | [1]
Aux boiler NG consumed per MWh | 0.16205 | kg/MWh | The power plant is able to produce 1MWh of power in a fraction of an hour (actually 0.1 minutes), so the auxiliary boiler operation is scaled accordingly and also scaled due to the fraction of an hour that the plant is operating (85%).

## Conversions
Conversions
Conversion Factors |  |  |  | References
1 | lb NG@STP | 23.8 | SCF NG | [2]
1 | kg | 2.2046 | lbm
1 | hr | 60 | minutes
1 | l | 0.26417 | gal
1 | day | 0.0027379 | yr
1 | hr | 0.041667 | day
1 | m3 | 1000 | l
1 | ton | 2000 | lbm

## Assumptions
Assumptions
Assumption # | Description
1 | Auxiliary boiler operates 50% of the time during plant shutdown periods
2 | Auxiliary boiler emissions are not captured

## Chart
Process
Upstream Emissions Data
Key
Electric Power
Operation of NETL Baseline SubCPC Power Plant: System Boundary
The operations of the NETL baseline Subcritical Pulverized Coal (SubCPC) power plants with or without carbon capture and sequestration (CCS) on the basis of 1 MWh electricity output.
Gypsum
Carbon dioxide
SubCPC power plant construction
Hard Coal (Illinois No 6)
Natural gas combustion in auxiliary boiler
Water (municipal)
Activated carbon
Limestone
Hydrate Lime
Ammonia
SCR catalyst
Triethylene glycol
Makeup water treatment chemicals [Material]