## Info
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
DS Sheet Information
|  | Process Name: | Operation of NETL Baseline SCPC Power Plant
|  | Process Description: | The operations of the NETL baseline Supercritical Pulverized Coal (SCPC) power plants with or without carbon capture and sequestration (CCS) on the basis of 1 MWh electricity output.
|  | Files: | This unit process is composed of this document and the file, DF_Stage-3-O-SCPC_Power_Plant_Baseline.docx, which provides additional details regarding calculations, data quality, and references as relevant.
|  | Summary and Calculations Worksheets: | As shown below, this document contains 3 summary worksheets (Data Summary, Reference Source Info, and DQI) that have been formatted consistent with NETL standards. The remaining 'calculations' worksheets are workspaces used by NETL engineers during the production of this unit process. The 'calculations' worksheets are presented for the convenience of the reader, and have not been subjected to standardized formatting.
This data sheet is organized as follows:
|  | Worksheet | Description
| Summary | Data Summary | Summary of Calculations, Input and Output Flows, Reference Flow, and other information
|  | Parameter Scenarios | Parameters for various scenarios where the unit process is used
|  | Reference Source Info | Referenced citations; citations are referenced by number, listed at the top of the Reference Source Info sheet
|  | DQI | Data Quality Index
| Calculations | Baseline | Baseline emissions data
|  | Lead | Lead emissions data
|  | Aux Boiler | Natural gas use in auxiliary boiler
|  | NH3 Emissions | Ammonia emission calculations
|  | Conversions | Unit Conversions
|  | Assumptions | Assumptions
|  | GaBi Import | Data Summary page formatted for importation into the GaBi 4.4 software
How to Cite This Document:
This document should be cited as: NETL (2012). NETL Life Cycle Inventory Data – Unit Process: Operation of NETL Baseline SCPC Power Plant. U.S. Department of Energy, National Energy Technology Laboratory. Last Updated: September 2012 (version 01). www.netl.doe.gov/energy-analyses (http://www.netl.doe.gov/energy-analyses)
Additional Notes:
|  | For the calculations sheets, values |  | highlighted in yellow | are also pulled forward into the 'Data Summary' sheet
Bibliographic references & assumptions referenced by number; see 'Reference Source Info' & 'Assumptions' sheets for cross-reference.
Data Summary sheet color coding: white indicates data input by model engineer; blue indicates automatically calculated values
Abbreviations used throughout this DS: INSERT AS RELEVANT
Disclaimer:
Template Version:
1.0
Neither the U.S. Department of Energy (DOE) National Energy Technology Laboratory (NETL) nor any person acting on behalf of these organizations:
A. Makes any warranty or representation, express or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that the use of any information, apparatus, method, or process disclosed in this document may not infringe on privately owned rights; or
B. Assumes any liability with this report as to its use, or damages resulting from the use of any information, apparatus, method, or process disclosed in this document.
Reference herein to any specific commercial product, process, or service by trade name, trademark, manufacturer, or otherwise, does not necessarily constitute or imply its endorsement, recommendation, or favoring by NETL. The views and opinions of the authors expressed herein do not necessarily state or reflect those of NETL.

## Data Summary
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
Data Module Summary
Process Name: |  | Operation of NETL Baseline SCPC Power Plant
Reference Flow: |  | 1 | MWh | of | Electricity | [5 empty] | DQI | 2,2,3,1,2 | (see DQI sheet for explanation)
Brief Description: |  | The operations of the NETL baseline Supercritical Pulverized Coal (SCPC) power plants with or without carbon capture and sequestration (CCS) on the basis of 1 MWh electricity output.
SECTION I: META DATA
Geographical Coverage: |  | USA |  |  | Goal and Scope:
Region |  | Midwest |  |  | Reference Flow: 1 MWh of Electricity
Year Data Best Represents: |  | 2010
Process Type: |  | Energy Conversion (EC) |  |  | This unit process provides a summary of relevant input and output flows associated with the production of electricity by the combustion of coal in the supercritical pulverized coal power plants defined in the NETL baseline studies. This process can be used for scenarios with and without CCS. Key inputs include Illinois No. 6 coal and water from surface and ground sources and combustion of natural gas in an auxiliary boiler. Key outputs include electricity, greenhouse gas emissions to air, and waste water.
Process Scope: |  | Gate-to-Gate Process (GG)
Allocation Applied: |  | No
Completeness: |  | Individual Relevant Flows Captured
Flows Aggregated in Data Set: |  |  |  |  | Note: All inputs and outputs are normalized per the reference flow (e.g., per MWh of electricity)
SECTION II: PARAMETERS
This section includes adjustable parameters, calculations needed to support adjustable parameters, and flow calculations based upon adjustable parameters.
| Parameter Name | Formula | Value | Min. Value | Max. Value | Unit | References | Comments
2 | CF |  | 0.85 |  |  |  | 1 | [dimensionless] Capacity Factor of SCPC plant
3 | CCS |  | 1 |  |  |  |  | [binary] If CO2 in flue gas is routed to CO2 recovery, value = 1. If CO2 in flue gas is released to atmosphere, value = 0.
12 | Net_MW_noCCS |  | 549.99 |  |  | MWh | 1 | [MWh] Net Power Output for a single hour of SCPC without CCS operation
10 | Net_MW_CCS |  | 549.97 |  |  | MWh | 1 | [MWh] Net Power Output for a single hour of SCPC with CCS operation
6 | Net_MW | IF(CCS=1;Net_MW_CCS;Net_MW_noCCS) | 549.97 |  |  | MWh |  | [MWh] Net Power Output for a single hour of SCPC operation with or without CCS, depending on value of "CCS" parameter
9 | Life_time |  | 30 |  |  | yrs |  | [Years] Life time of a power plant
6 | Plants | 1/(Life_time*365.25*24*Net_MW*CF) | 8.1343e-09 |  |  | pce/MWh |  | [Piece/MWh] Fraction of a power plant per MWH
15 | SCPC_CO2caprate |  | 0.9 |  |  |  | 1 | [dimensionless] Fraction of CO2 captured
12 | SCPC_CO2_CCS |  | 110.6765 |  |  | kg/MWh | 1 | [kg/MWh] CO₂ emissions to air per MWh with CCS
14 | SCPC_CO2_noCCS |  | 801.9513 |  |  | kg/MWh | 1 | [kg/MWh] CO₂ emissions to air per MWh without CCS
8 | SCPC_CO2 | IF(CCS=1;SCPC_CO2_CCS;SCPC_CO2_noCCS) | 110.6765 |  |  | kg/MWh |  | [kg/MWh] CO₂ emissions to air per MWh without or without CCS, depending on value of "CCS" parameter
12 | SCPC_CO2_cap | IF(CCS=1;(SCPC_CO2*SCPC_CO2caprate/(1-SCPC_CO2caprate); 0) | 996.0888 |  |  | kg/MWh |  | [kg/MWh] CO₂ captured for CCS
12 | SCPC_NOx_CCS |  | 0.38101 |  |  | kg/MWh | 1 | [kg/MWh] NOx emissions to air per MWh with CCS
14 | SCPC_NOx_noCCS |  | 0.27572 |  |  | kg/MWh | 1 | [kg/MWh] NOx emissions to air per MWh without CCS
8 | SCPC_NOx | IF(CCS=1;SCPC_NOx_CCS;SCPC_NOx_noCCS) | 0.38101 |  |  | kg/MWh |  | [kg/MWh] NOx emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | SCPC_SO2_CCS |  | 0.0088557 |  |  | kg/MWh | 1 | [kg/MWh] SO₂ emissions to air per MWh with CCS
14 | SCPC_SO2_noCCS |  | 0.33809 |  |  | kg/MWh |  | [kg/MWh] SO₂ emissions to air per MWh without CCS
8 | SCPC_SO2 | IF(CCS=1;SCPC_SO2_CCS;SCPC_SO2_noCCS) | 0.0088557 |  |  | kg/MWh |  | [kg/MWh] SO₂ emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
11 | SCPC_PM_CCS |  | 0.070518 |  |  | kg/MWh | 1 | [kg/MWh] PM emissions to air per MWh with CCS
13 | SCPC_PM_noCCS |  | 0.051218 |  |  | kg/MWh |  | [kg/MWh] PM emissions to air per MWh without CCS
7 | SCPC_PM | IF(CCS=1;SCPC_PM_CCS;SCPC_PM_noCCS) | 0.070518 |  |  | kg/MWh |  | [kg/MWh] PM emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
11 | SCPC_Hg_CCS |  | 6.2318e-06 |  |  | kg/MWh | 1 | [kg/MWh] Hg emissions to air per MWh with CCS
13 | SCPC_Hg_noCCS |  | 4.5043e-06 |  |  | kg/MWh |  | [kg/MWh] Hg emissions to air per MWh without CCS
7 | SCPC_Hg | IF(CCS=1;SCPC_Hg_CCS;SCPC_Hg_noCCS) | 6.2318e-06 |  |  | kg/MWh |  | [kg/MWh] Hg emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
7 | SCPC_Pb_CCS |  | 7.053e-05 |  |  | kg/MWh | 1,2,3 | [kg/MWh] Pb emissions to air per MWh with CCS
| SCPC_Pb_noCCS |  | 6.1762e-05 |  |  | kg/MWh | 1,2,3 | [kg/MWh] Pb emissions to air per MWh without CCS
| SCPC_Pb | IF(CCS=1;SCPC_Pb_CCS;SCPC_Pb_noCCS) | 7.053e-05 |  |  | kg/MWh |  | [kg/MWh] Lead emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | SCPC_NH3_CCS |  | 0.0026988 |  |  | kg/MWh | 7,8,9 | [kg/MWh] Ammonia emissions to air per MWh with CCS
14 | SCPC_NH3_noCCS |  | 0.0019536 |  |  | kg/MWh | 7,8,9 | [kg/MWh] Ammonia emissions to air per MWh without CCS
8 | SCPC_NH3 | IF(CCS=1;SCPC_NH3_CCS;SCPC_NH3_noCCS) | 0.0026988 |  |  | kg/MWh |  | [kg/MWh] Ammonia emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
13 | SCPC_coal_CCS |  | 466.6648 |  |  | kg/MWh | 1 | [kg/MWh] Coal consumption per MWh with CCS
15 | SCPC_coal_noCCS |  | 337.7494 |  |  | kg/MWh | 1 | [kg/MWh] Coal consumption per MWh without CCS
9 | SCPC_coal | IF(CCS=1;SCPC_coal_CCS;SCPC_coal_noCCS) | 466.6648 |  |  | kg/MWh |  | [kg/MWh] Coal consumption per MWh with or without CCS, depending on value of "CCS" parameter
13 | SCPC_H2OinCCS |  | 4156.3821 |  |  | L/MWh | 1 | [L/MWh] Water withdrawal with CCS
15 | SCPC_H2OinnoCCS |  | 2203.1097 |  |  | L/MWh | 1 | [L/MWh] Water withdrawal without CCS
10 | SCPC_H2Oin | IF(CCS=1;SCPC_H2OinCCS;SCPC_H2OinnoCCS) | 4156.3821 |  |  | L/MWh |  | [L/MWh] Water withdrawal with or without CCS, depending on value of "CCS" parameter
13 | SCPC_H2OinGnd | SCPC_H2Oin/2 | 2078.1911 |  |  | L/MWh | 1 | [L/MWh] Ground water withdrawal
14 | SCPC_H2OinSurf | SCPC_H2Oin/2 | 2078.1911 |  |  | L/MWh | 1 | [L/MWh] Surface water withdrawal
14 | SCPC_H2OoutCCS |  | 976.6362 |  |  | L/MWh | 1 | [L/MWh] Waste water with CCS
15 | SCPC_H2OoutnCCS |  | 454.2494 |  |  | L/MWh | 1 | [L/MWh] Waste water without CCS
11 | SCPC_H2Oout | IF(CCS=1;SCPC_H2OoutCCS;SCPC_H2OoutnCCS) | 976.6362 |  |  | L/MWh |  | [L/Mwh] Waster water with or without CCS, depending on value of "CCS"Parameter
7 | CF_AuxB |  | 0.5 |  |  |  | 1 | [Dimensionless] Fraction of downtime that auxliary boiler operates
15 | AuxB_opt_factor | (1-CF)*CF_AuxB | 0.075 |  |  |  | 1 | [Dimensionless] Fraction of total time that auxiliary boiler operates
14 | NG_AuxB_tot_kg |  | 1010.1009 |  |  | kg/hr | 6 | [kg/hr] Natural gas consumption for auxiliary boiler
7 | NG_AuxB | (AuxB_opt_factor*NG_AuxB_tot_kg)/(Net_MW*CF) | 0.16206 |  |  | kg/MWh |  | [kg/MWh] Natural gas consumption in auxiliary boiler
| End of List | <select this entire row, then insert new row>
SECTION III: INPUT FLOWS
This section includes all input flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
| Plants | SCPC power plant [Construction] | 1 | kg | 8.1343e-09 | pce/MWh | 8.1343e-09 | kg | X |  | 1 | [Technosphere] SCPC power plant
| SCPC_coal | Hard Coal (Illinois No 6) [Hard coal (resource)] | 1 | kg | 466.6648 | kg/MWh | 466.6648 | kg | X |  | 1 | [Technosphere] Coal for combustion
| NG_AuxB | Natural gas combustion in auxiliary boiler | 1 | kg | 0.16206 | kg/MWh | 0.16206 | kg | X |  | 1,6 | [Technosphere] Natural gas combusted in auxiliary boiler
| SCPC_H2OinGnd | Water (ground water) [Water] | 1 | L | 2078.1911 | L/MWh | 2078.1911 | L |  |  | 1 | [Resource] Ground water withdrawal
| SCPC_H2OinSurf | Water (surface water) [Water] | 1 | L | 2078.1911 | L/MWh | 2078.1911 | L |  |  | 1 | [Resource] Surface water withdrawal
| End of List | <select this entire row, then insert new row> | Factor |  |  |  | Amount |  |  | <select from list>
SECTION IV: OUTPUT FLOWS
This section includes all output flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
|  | Power [Electric Power] | 1 | MWh | 1 |  | 1 |  |  |  |  | Reference flow
| SCPC_CO2_cap | Carbon dioxide [Inorganic intermediate products] | 1 | kg | 996.0888 | kg/MWh | 996.0888 | kg | X |  | 1 | CO₂ captured for CCS
| SCPC_CO2 | Carbon dioxide [Inorganic emissions to air] | 1 | kg | 110.6765 | kg/MWh | 110.6765 | kg |  |  | 1 | Emission to air
| SCPC_NOx | Nitrogen oxides [Inorganic emissions to air] | 1 | kg | 0.38101 | kg/MWh | 0.38101 | kg |  |  | 1 | Emission to air
| SCPC_SO2 | Sulphur dioxide [Inorganic emissions to air] | 1 | kg | 0.0088557 | kg/MWh | 0.0088557 | kg |  |  | 1 | Emission to air
| SCPC_PM | Dust (unspecified) [Particles to air] | 1 | kg | 0.070518 | kg/MWh | 0.070518 | kg |  |  | 1 | Emission to air
| SCPC_Pb | Lead (+II) [Heavy metals to air] | 1 | kg | 7.053e-05 | kg/MWh | 7.053e-05 | kg |  |  | 1,2,3 | Emission to air
| SCPC_Hg | Mercury (+II) [Heavy metals to air] | 1 | kg | 6.2318e-06 | kg/MWh | 6.2318e-06 | kg |  |  | 1 | Emission to air
| SCPC_NH3 | Ammonia [Inorganic emissions to air] | 1 | kg | 0.0026988 | kg/MWh | 0.0026988 | kg |  |  | 7,8,9 | Emission to air
| SCPC_H2Oout | Water (wastewater) [Water] | 1 | L | 976.6362 | L/MWh | 976.6362 | L |  |  | 1 | Renewable resources
| End of List | <select this entire row, then insert new row> | Factor | [6 empty] | <select from list>
Detailed Spreadsheet Lists
| Process Type | Process Scope | Completeness |  |  | Origin |  | Tracked
| <select from list> | <select from list> | <select from list> |  |  | <select from list>
| Extraction Process (EP) | Cradle-to-Grave (End-of-Life) Process (CE) | All Flows Captured |  |  | Measured |  | X
| Manufacturing Process (MP) | Cradle-to-Gate Process (CG) | All Relevant Flows Captured |  |  | Calculated |  | *
| Installation Process (IP) | Gate-to-Gate Process (GG) | Individual Relevant Flows Captured |  |  | Literature
| Basic Process (BP) | Gate-to-Grave (End-of-Life) Process (GE) | Some Relevant Flows Not Captured |  |  | Estimated
| Energy Conversion (EC) |  | No Statement |  |  | No Statement
Transport Process (TP)
Recovery Process (RP)
Waste Treatment Process (WT)
Auxiliary Process (AP)
Note on D83: Robert Eckard: Please insert appropriate info in the brackets. Original formula is =concatenate(G5," [Insert]")
Note on D87: 548788: Do not double count SO2 in SOx flow. Use the
Note on D88: 548788: Do not double count PM between dust flows. PM data should be reported as defined in data source (PM2.5 separate from PM10 when available). If this definition is not available, inventory as PM unspecified.

## PS
Parameter Scenarios
| Parameter Name | Enter a Scenario ID below: | Scenario ID |  |  | [Units] Comments
|  | 3 | 1 | 2 | 3
|  | Operation of NETL Baseline SCPC Power Plant | Operation of NETL Baseline SCPC Power Plant
|  | Scenario 3 Name | Scenario 1 Name | Scenario 2 Name | Scenario 3 Name
| <Enter Parameters> | 0 |  |  |  | <Add comments from Data Summary Sheet>
| <for the Scenarios> | 0
0
0
0
0
0
Scenario Descriptions:
| Scenario ID | Description
| 1 | <Add detailed description to the Scenarios>
2
3
The purpose of this "Parameters Scenarios" worksheet is to provide a flexible method for adjusting parameters within this unit process. The above table allows you to select a scenario ID (CELL C4) and uses a lookup function to populate the adjustable parameters (the cells with yellow shading). The values for the adjustable parameters are linked to the "Data Summary" sheet.

## Reference Source Info
Field Name
Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
SourceType | Separate Publication | Separate Publication | Separate Publication | Separate Publication | Separate Publication | Separate Publication | Separate Publication | Undefined | Separate Publication | Separate Publication | Separate Publication
Title | Cost and Performance Baseline for Fossile Energy Plants Revision 2 | Toxic Releases Inventory | Existing Generating Unit in the United States by State and Energy Source, 2010 | Genoa Site | Coal-Fired Plants in Indiana | 40000 PPH Nebraska, Watertube, trailer mounted, 350 psi, gas/oil (3) | SCR Catalyst Management Strategies to Reduce Operating Expenses. | Selective Catalytic Reduction - SCR - Catalyst Management - NOx Control Systems | Isothermal Properties for Ammonia | Ventyx Velocity Suite | The Emissions and Generation Resource Integrated Database (eGRID)
FirstAuthor | Woods, Mark C., | EPA | U.S. Energy Information Administration | Dairlyland Power Cooperative | Industcards | Wabash Power Equipment Co | Stanley Mack | Babcock Power | NIST | Ventyx | EPA
AdditionalAuthors | Pamela J. Capicotto, John L. Haslbeck, Norma J. Kuehn, Michael Matuszewski, Lora L. Pinkerton, Michael D. Rutkowski, Ronald L. Schoff, Vladimir Vaysman. | [5 empty] | Joseph Patchett
Year | 2010 | 2012 | 2011 | 2003 | 2012 | 2008 | 1997 | 2009 | 2011 | 2012 | 2012
Date
PlaceOfPublication | Pittsburgh, PA |  |  |  |  | Wheeling, IL | NETL | Internet | Internet
Publisher | DOE, National Energy Technology Laboratory | EPA | EIA | Dairlyland Power Cooperative | Industcards
PageNumbers
Table or Figure Number
NameOfEditors
TitleOfAnthology
Journal
VolumeNo
IssueNo
Docket Number
Copyright | [9 empty] | 2012
Internet Address | http://www.netl.doe.gov/energy-analyses/pubs/BitBase_FinRep_Rev2.pdf | http://www.epa.gov/enviro/facts/tri/search.html | http://www.eia.gov/electricity/capacity/xls/existing_gen_units_2010.xls | http://www.dairynet.com/energy_resources/genoa.pdf | http://www.industcards.com/st-coal-usa-in.htm |  | http://www.netl.doe.gov/publications/proceedings/97/97ncr/mack.pdf | http://www.babcockpower.com/index.php?option=products&task=viewproduct&coid=17&proid=45 | http://webbook.nist.gov/chemistry/fluid/
Internet Access Date | August 14, 2012 | August 14, 2012 | August 15, 2012 | August 15, 2012 |  |  |  | No Statement | August 8, 2012 | August 15, 2012
Data Type (Origin) | Literature | Database | Database | Literature | Literature | Literature | Literature | N/A | Database | Database
Year Data Represents |  | 2006-2011 | 2010 | 2003 | 2012 | Estimated 1999 | Estimated 1997 | N/A | 2011 | 2012
Geographical Representation | USA | USA | USA | USA | Indiana, USA |  | N/A | N/A | N/A | Midwest
Representativeness | Average industry | Specific site data | Specific site data | Single site information | Single site information | Product Representative from Brochure
BibliographicText | Woods, Mark C.,, 2010. Cost and Performance Baseline for Fossile Energy Plants Revision 2, DOE, National Energy Technology Laboratory, Pittsburgh, PA. Accessed on August 14, 2012 at http://www.netl.doe.gov/energy-analyses/pubs/BitBase_FinRep_Rev2.pdf. | EPA, 2012. Toxic Releases Inventory, EPA, . Accessed on August 14, 2012 at http://www.epa.gov/enviro/facts/tri/search.html. | U.S. Energy Information Administration, 2011. Existing Generating Unit in the United States by State and Energy Source, 2010, EIA, . Accessed on August 15, 2012 at http://www.eia.gov/electricity/capacity/xls/existing_gen_units_2010.xls. | Dairlyland Power Cooperative, 2003. Genoa Site, Dairlyland Power Cooperative, . Accessed on August 15, 2012 at http://www.dairynet.com/energy_resources/genoa.pdf. | Industcards, 2012. Coal-Fired Plants in Indiana, Industcards, . Accessed on at http://www.industcards.com/st-coal-usa-in.htm. | Wabash Power Equipment Co, 2008. 40000 PPH Nebraska, Watertube, trailer mounted, 350 psi, gas/oil (3), , Wheeling, IL. Accessed on at . | Stanley Mack, 1997. SCR Catalyst Management Strategies to Reduce Operating Expenses. , , NETL. Accessed on at http://www.netl.doe.gov/publications/proceedings/97/97ncr/mack.pdf. | Babcock Power, 2009. Selective Catalytic Reduction - SCR - Catalyst Management - NOx Control Systems, , Internet. Accessed on No Statement at http://www.babcockpower.com/index.php?option=products&task=viewproduct&coid=17&proid=45. | NIST, 2011. Isothermal Properties for Ammonia, , Internet. Accessed on August 8, 2012 at http://webbook.nist.gov/chemistry/fluid/. | Ventyx, 2012. Ventyx Velocity Suite, , . Accessed on August 15, 2012 at . | EPA. (2012). The Emissions and Generation Resource Integrated Database (eGRID). EPA, from http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html
Text/Description | Specifications and analysis results from baseline SCPC plants. | Lead emissions for 6 coal power plants | Name plate generating capacity for US power plants | States that Genoa facility is supercritical | States that Gibson facility is supercritical |  | Figure 4, average live span of SCR catalyst | Shows semi-linear relationship between catalyst life and ammonia slip
Reference Source Info Lists
Source Type
<select from list>
Undefined
Article
Chapters in Anthology
Separate Publication
Measurement on Site
Oral Communication
Personal Written Communication
Questionnaires

## DQI
Data Quality Index
DQI Determination
| Input/Output | Reference (see 'Reference Source Info' worksheet) | Source Reliability | Completeness | Temporal Correlation | Geographical Correlation | Technical Correlation | DQI | Recommendations | Determinations
| Coal for combustion | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2 | Requirements met | OK
| Aux boiler natural gas | 1,6 | 2 | N/A | 1 | 1 | 2 | 2,N/A,1,1,2 | Requirements met | OK
| Water withdrawal | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2 | Requirements met | OK
| CO2 for capture | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2
| CO2 emissions | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2
| SO2 emissions | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2
| Particulate matter emissions | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2
| Lead emissions | 1,2,3 | 1 | 2 | 1 | 1 | 1 | 1,2,1,1,1
| Mercury Emissions | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2
| Ammonia emissions | 7,8,9 | 1 | 2 | 3 | N/A | 2 | 1,2,3,N/A,2
| Water discharge | 1 | 1 | 1 | 1 | 1 | 2 | 1,1,1,1,2
[8 empty] | 0,0,0,0,0 | Requirements met | OK
| Total | [6 empty] | 2,2,3,1,2
DQI Methodology
DQI Matrix (from NETL LCI&C Guideline Document, adapted from Weidema and Wenaes)
| Indicator | Score
|  | 1 | 2 | 3 | 4 | 5
| Source Reliability (for most applications, source quality guidelines only factor) | data verified based on measurements | data verified based on some assumptions and/or standard science and engineering calculations | data verified with many assumptions, or non-verified but from quality source | qualified estimate | non-qualified estimate
|  | source quality guidelines met |  | source quality guidelines not met
|  | data cross checks, greater than or equal to 3 quality sources | 2 or less data sources available for cross check, or data sources available that do not meet quality standards |  | no data available for cross check
| Completeness | representative data from a sufficient sample of sites over an adequate period of time | smaller number of site but an adequate period of time | sufficient number of sites but a less adequate period of time | smaller number of sites and shorter periods or incomplete data from an adequate number of sites or periods | representativeness unknown or incomplete data sets
| Temporal Correlation | less than three years of difference to year of study/current year | less than 6 years of difference | less than 10 years difference | less than 15 years difference | age of data unknown or more than 15 years difference
| Geographical Correlation | data from area under study | average data from larger area or specific data from a close area | data from area with similar production conditions | data from area with slightly similar production conditions | data from unknown area or area with very different production conditions
| Technological Correlation | data from technology, process or materials being studied | data from a different technology using the same process and/or materials |  | data on related process or material using the same technology | data or related process or material using a different technology
Indicator Descriptions
Source Reliability -- This indicator relates to the quality of the data source and the verification of the data collection methods used within the source.
Data Verification -- Source data that have been verified within error bounds by either the source author (with a high level of transparency) or the LCI modeler. Verification can be done by measurement, including on-site checking, recalculation, or mass or energy balance analysis. If the source data cannot be verified without making assumptions (i.e., not enough data are available to close the mass/energy balance), then the score should be a 2 or 3, depending on the number of assumptions. If no source data are available, a qualified estimate from an expert in the field should receive a score of 4, and an estimate from a non-expert should receive a score of 5. Mostly applicable to primary data.
Source Quality Guidelines -- The highest quality source should be
o From a peer reviewed journal or a government sponsored study. If the source is an LCA, it must meet ISO requirements.
o Publicly available either for free or at cost, or directly representative of the process of interest.
o Written/published by an unbiased party.
o An unbiased survey of experts or process locations.
When the source used for data is a reputable model that does not specifically meet the above criteria, it is the discretion of the modeler to determine the rank of the source. An example for justification would be if the data have been used in published reports that met the data quality standards.
Data Cross-Check -- The number of sources that verify the same data point or series, within reason. As a general benchmark, a high standard is greater than or equal to three data cross checks with quality approved sources. This typically refers to primary data, and if no other data sources are available, this can be omitted.
Completeness -- This indicator quantifies the statistical robustness of the source data. This ranking is based on how many data points were taken, how representative the sample is to the studied process, and whether the data were taken for an acceptable time period to even out normal process fluctuations. The following examples are given to help clarify this indicator.
Temporal Correlation -- This indicator represents how well the time period in which the data were collected corresponds with the year of the study. If the study is set to evaluate the use of a technology from 2000 to 2040, data from 1970 would not be very accurate. It is important when assigning this ranking to take notice of any discrepancies between the year the source was published and the year(s) the data were collected.
Geographical Correlation -- This indicator represents the appropriateness between the region of study and the source data region. This indicator becomes important when comparing data from different countries. For example, technological advances might reasonably be expected to develop differently in different countries, so efficiency and energy use might be very different. This is also important when looking at best management practices for carbon mitigation.
Technological Correlation -- This indicator embodies all other differences that may be present between the study goals and the data source. From the above example, using data for a type of biomass that is not being studied in the LCA should result in a lower technological representativeness ranking.
Steps for Applying DQM
1) Calculate score for each unit process (UP) input. If more than one reference source is used for one input, and the score is lower, consider both scores. If an indicator does not relate to a specific source, assume N/A. If all emissions come from one source, only one score is needed
- when a score is determined for a particular reference source, add to 'Reference Source Info' for future use
2) From the reference scores, determine the data quality indicator (DQI) for the unit process inputs for commissioning/decommissioning operations (when applicable)*
- the scores are not additive, rather, the lowest score for an indicator of a particular data input is the lowest score for the UP
3) Significant inputs of low quality unit processes (DQI mostly 3-5) should be varied to the minimum and maximum values or 95 percent confidence interval of the uncertainty range.
- check significance first. If the input is not significant by a long shot (or with the maximum possible value), it is not necessary to include in the UP
4) If the change in the final result from a single unit process is greater than a threshold value, for example, 0.1 g CO2e/MJ, then the processes should be flagged for possible additional data quality refinement
- for example, if emissions from the total steel inputs are found to be significant during sensitivity, the DQI will be performed on the steel profile. If this is not possible (because data are not transparent/purchased), it will be listed as a future recommendation
- if, however, the steel inputs are significant due to a large amount of steel needed for a particular process, then the DQI on that input should be performed and the data refined if needed
5) If the UP input is significant (with or without sensitivity), but no data refinement is possible, this is listed as a data limitation and noted in the report
* For NETL LCI&C studies, because data quality for construction is typically low, sensitivity on those inputs is already performed and the DQI does not need to be calculated. If sensitivity is not performed on construction, or sensitivity shows that a particular input is significant, then the DQI will be performed

## Baseline
Baseline
Calculations | [5 empty] | References
Emissions w/o CCS
Flow | Value | Units | Notes | Assumptions
CO2 | 1768 | lb/MWhnet |  |  |  | [1]
CO2 | 801.9513 | kg/MWhnet | Emissions per net MWh
Gross Power Output | 580.4 | MWhgross | Gross power output for 1 hour |  |  | [1]
Net Power Output | 549.99 | MWhnet | Net power output for 1 hour |  |  | [1]
NOx | 0.576 | lb/MWhgross |  |  |  | [1]
NOx | 0.26127 | kg/MWhgross
NOx | 0.27572 | kg/MWhnet | Emissions per net MWh
SO2 | 0.7063 | lb/MWhgross |  |  |  | [1]
SO2 | 0.32037 | kg/MWhgross
SO2 | 0.33809 | kg/MWhnet
PM | 0.107 | lb/MWhgross |  |  |  | [1]
PM | 0.048534 | kg/MWhgross
PM | 0.051218 | kg/MWhnet
Hg | 9.41e-06 | lb/MWhgross |  |  |  | [1]
Hg | 4.2683e-06 | kg/MWhgross
Hg | 4.5043e-06 | kg/MWhnet
Coal Flowrate | 409528 | lb/hr |  |  |  | [1]
Coal Flowrate | 185758.7761 | kg/hr
Coal Flowrate | 337.7494 | kg/MWhnet
Raw water withdrawal | 9.7 | gpm/MWnet |  |  |  | [1]
Raw water withdrawal | 582 | gal/MWhnet
Raw water withdrawal | 2203.1097 | L/MWhnet
Water discharge | 2 | gpm/MWnet |  |  |  | [1]
Water discharge | 120 | gal/MWhnet
Water discharge | 454.2494 | L/MWhnet
Emissions w/ CCS
CO2 | 244 | lb/MWhnet |  |  |  | [1]
CO2 | 110.6765 | kg/MWhnet | Emissions per net MWh
Gross Power Output | 662.8 | MWhgross | Gross power output for 1 hour |  |  | [1]
Net Power Output | 549.97 | MWhnet | Net power output for 1 hour |  |  | [1]
NOx | 0.697 | lb/MWhgross |  |  |  | [1]
NOx | 0.31615 | kg/MWhgross
NOx | 0.38101 | kg/MWhnet | Emissions per net MWh
SO2 | 0.0162 | lb/MWhgross |  |  |  | [1]
SO2 | 0.0073482 | kg/MWhgross
SO2 | 0.0088557 | kg/MWhnet
PM | 0.129 | lb/MWhgross |  |  |  | [1]
PM | 0.058513 | kg/MWhgross
PM | 0.070518 | kg/MWhnet
Hg | 1.14e-05 | lb/MWhgross |  |  |  | [1]
Hg | 5.171e-06 | kg/MWhgross
Hg | 6.2318e-06 | kg/MWhnet
Coal Flowrate | 565820 | lb/hr |  |  |  | [1]
Coal Flowrate | 256651.6348 | kg/hr
Coal Flowrate | 466.6648 | kg/MWhnet
Raw water withdrawal | 18.3 | gpm/MWnet |  |  |  | [1]
Raw water withdrawal | 1098 | gal/MWhnet
Raw water withdrawal | 4156.3821 | L/MWhnet
Water discharge | 4.3 | gpm/MWnet |  |  |  | [1]
Water discharge | 258 | gal/MWhnet
Water discharge | 976.6362 | L/MWhnet

## Lead
Lead Data
EPA Lead Emissions Data (Flue Gas) Reference [2]
Plant Name [Reference 3] | Generator ID [Reference 3] | Supercritical Reference [10] | 2009 Production (MWh) Reference [11] | 2007 Production (MWh) Reference [11] | 2005 Production (MWh) Reference [11] | Average (MWh) | Energy Source 1 [Reference 3] | Energy Source 2 [Reference 3] | Initial Month of Operation [Reference 3] | Initial Year of Operation [Reference 3] | Unit Status [Reference 3] | TRI # / URL | Lead Air Stack 2011 | 2010 | 2009 | 2008 | 2007 | 2006 | average lbs/yr | Total Annual Lead Emitted to Air, per Average Production (kg/MWh)
Cardinal | 1 | Y | 10784462 | 10709665.999 | 11372176 | 10955434.6663 | BIT |  | 2 | 1967 | OP | 43913CRDNL306CO | 188 | 342 | 514 | 535 | 691 | 576 | 474.3333 | 4.3297e-05
Cardinal | 2 | Y |  |  |  |  | BIT |  | 7 | 1967 | OP
Cardinal | 3 | Y |  |  |  |  | BIT |  | 9 | 1977 | OP
Conemaugh | 1 | Y | 12155841 | 12956157.002 | 12942074 | 12684690.6673 | BIT |  | 5 | 1970 | OP | 15944CNMGHRTE20 | 217.4 | 260 | 620 | 1800 | 2031 | 2243 | 1195.2333 | 9.4226e-05
Conemaugh | 2 | Y |  |  |  |  | BIT |  | 5 | 1971 | OP
FirstEnergy Bruce Mansfield | 1 | Y | 17390613 | 17812664.999 | 18343905 | 17849060.9997 | BIT |  | 4 | 1976 | OP | 15077FRSTNOFFRT | 1130 | 1320 | 1330 | 1400 | 1410 | 2000 | 1431.6667 | 8.021e-05
FirstEnergy Bruce Mansfield | 2 | Y |  |  |  |  | BIT |  | 10 | 1977 | OP
FirstEnergy Bruce Mansfield | 3 | Y |  |  |  |  | BIT |  | 9 | 1980 | OP
FirstEnergy Eastlake | 5 | Y | 5399583 | 7151316.002 | 8380920 | 6977273.0007 | BIT | SUB | 9 | 1972 | OP | 44095FRSTN10ERI | 223 | 213 | 227 | 274 | 275 | 336 | 258 | 3.6977e-05
FirstEnergy Fort Martin Power Station | 1 | Y | 4085340 | 6877539 | 7060817 | 6007898.6667 | BIT | DFO | 10 | 1967 | OP | 26541FRTMRRTE53 | 195 | 108 | 39.9 | 92.3 | 74.4 | 102 | 101.9333 | 1.6967e-05
FirstEnergy Fort Martin Power Station | 2 | Y |  |  |  |  | BIT | DFO | 12 | 1968 | OP
FirstEnergy Harrison Power Station | 1 | Y | 10063605 | 13796514.001 | 13212140 | 12357419.667 | BIT | DFO | 12 | 1972 | OP | 26366HRRSNRTE20 | 435 | 534 | 433 | 505 | 615 | 430 | 492 | 3.9814e-05
FirstEnergy Harrison Power Station | 2 | Y |  |  |  |  | BIT | DFO | 12 | 1973 | OP
FirstEnergy Harrison Power Station | 3 | Y |  |  |  |  | BIT | DFO | 12 | 1974 | OP
FirstEnergy Pleasants Power Station | 1 | Y | 5767553 | 7857732 | 8851063 | 7492116 | BIT | DFO | 4 | 1979 | OP | 26134PLSNTNO1PO | 243 | 250 | 169 | 257 | 387 | 484 | 298.3333 | 3.982e-05
FirstEnergy Pleasants Power Station | 2 | Y |  |  |  |  | BIT | DFO | 12 | 1980 | OP
General James M Gavin | 1 | Y | 19160246 | 18958853 | 19142304 | 19087134.3333 | BIT |  | 10 | 1974 | OP | 45620MRCNL7397N | 567 | 655 | 671 | 1372 | 1247 | 1053 | 927.5 | 4.8593e-05
General James M Gavin | 2 | Y |  |  |  |  | BIT |  | 7 | 1975 | OP
Gibson | 1 | Y | 18901781 | 23342346.998 | 22442805 | 21562310.9993 | BIT |  | 5 | 1976 | OP | 47670PSNRGHWY64 | 765.2 | 1290.1 | 1686.6 | 2394.1 | 2784.2 | 2816 | 1956.0333 | 9.0715e-05
Gibson | 2 | Y |  |  |  |  | BIT |  | 4 | 1975 | OP
Gibson | 3 | Y |  |  |  |  | BIT |  | 3 | 1978 | OP
Gibson | 4 | Y |  |  |  |  | BIT |  | 3 | 1979 | OP
Gibson | 5 | Y |  |  |  |  | BIT |  | 10 | 1982 | OP
Hatfields Ferry Power Station | 1 | Y | 9052402 | 10510804 | 8672997 | 9412067.6667 | BIT | DFO | 11 | 1969 | OP | 15461HTFLDRD1BO | 1080 | 874 | 928 | 1600 | 1380 | 1310 | 1195.3333 | 0.000127
Hatfields Ferry Power Station | 2 | Y |  |  |  |  | BIT | DFO | 10 | 1970 | OP
Hatfields Ferry Power Station | 3 | Y |  |  |  |  | BIT | DFO | 12 | 1971 | OP
[19 empty] | Average | 6.1762e-05 | Emission factor used for w/o CCS
Notes:
1. Lead emissions data is provided on a site-wide basis. This list of plants is comprised of plants/sites with only supercritical power plants. | [18 empty] | w/o CCS Gross Power Ref [1] | 580.4 | MW
[19 empty] | w/ CCS Gross Power Ref [1] | 662.8 | MW
[19 empty] | Emission factor scaled by ratio of gross power output | 7.053e-05 | Emission factor used for w/ CCS
References
Name | Type | Address | Description
EPA Facility Registry System | Dynamic Database | http://www.epa.gov/enviro/html/fii/fii_query_java.html | Provides an updated, searchable database of every registered power plant in the U.S. and their annual emissions levels. | Reference [2]
EIA Power Plants 2000 | Report | www.eia.gov/electricity/capacity/xls/existing_gen_units_2010.xls | Official EIA report listing every U.S. power plant by name, state, ownership, net capacity, and fuel type. Also provides national electricity production statistics. | Reference [3]

## Aux Boiler
Sheet Name Here
Calculations |  |  |  |  | References
Auxiliary Boiler
Auxiliary boiler NG consumption | 53000 | SCF/hr |  |  | [6] | This consumption rate is correlated with several other internet sources: | 54,650 SCF/hr | http://www.nationwideboiler.com/pdfs/specs/equipment/40KPPH700TM_G2_LN_B420.pdf
| 2226.8908 | lb/hr
| 1010.1007 | kg/hr
Time NGCC plant up | 0.85 | yr |  |  | [1] Capacity factor
or | 0.85 | hr
NGCC PLant downtime | 0.15 | hr
Fraction of downtime Aux. boiler runs | 0.5
| 0.075 | hr
Aux boiler NG consumption during downtime | 75.7575 | kg/hr
Power plant net output | 549.99 | MW |  |  | [1]
Aux boiler NG consumed per MWh | 0.16205 | kg/MWh | The 549.99 MW power plant is able to produce 1MWh of power in a fraction of an hour (actually 0.1 minutes), so the auxiliary boiler operation is scaled accordingly and also scaled due to the fraction of an hour that the plant is operating (85%).
Aux boiler alternative calculation
Power plant life | 30 | years
| 262980 | hours
Plant operating time | 223533 | hours | 85% of 30 years
Power plant total MWh | 122940914.67 | MWh | 549.990 MW * operating time
Downtime | 39447 | hours | 15% of 30 years
Aux boiler time | 19723.5 | hours | 50% of downtime
Aux boiler NG consumption | 19922720.2863 | kg | 1010.10 kg/hr * boiler time
Aux boiler NG consumption/MWh | 0.16205 | kg/MWh | total boiler NG consumption/Power plant total MWh

## NH3 Emissions
Raw Data
- Reference 1 (Baseline Report) reports no NH3 air emissions, only a 10 ppmv ammonia slip at the end of the useful life of catalyst
- slip rate (ppmv) - maximum from source | 2 | ppmv | Ref [1] pg. 384(PDF pg. 410)
- The Baseline report indicates the catalyst starts with one layer, with space for an additional layer; two layer system
- Figure 4 in Reference 7 gives typical catalyst replacement time for 3 layer system
- Figure from Reference 8 shows a typical relationship between catalyst strength and Slip Rate
Assumptions:
- As the catalyst degrades with age, the slip rate is known to increase. Because this slip rate was indicated for end-of-catalyst-life, we assume it is the maximum slip rate
For Simplicity we assume:
- a 2 year lifetime for each layer
- a linear relationship between slip rate and life where at year 0 slip rate is 0, at end of year 2 slip rate is 2
- Therefore, average slip rate of 1 ppmv throughout the lifetime of the plant
Slip rate (avg) = | 1 | ppmv
Reference [1] describes the SCR reactor as being located in the boiler.
Reference [1] also states that the optimum inlet flue gas temperature range for the catalyst is 260-455 degC. The ammonia emission rate below is calculated assuming
that temperature is at 400 degC and pressure is between 0.11 and 0.1 MPa (the pressures for the flue gas stream before and after the boiler.
Without CCS
Calculation
volume NH3/10^6 volume flue gas | 1e-06 | m^3 NH3/m^3 flue
flue gas (stream 4 to stack) | 1758073 | kg/hr | (Exhibit 5-4 from Baseline Report, pg. 454) Streams 2+5+7-3-6
flue gas density | 0.52302 | kg/m^3 | Density calculated below, between 0.1 and 0.11 MPa
flue gas volume flow rate | 3361413.0789 | m^3/hr
volume NH3/hr | 3.3614 | m^3/hr | based on 1ppmv
density NH3 @ 0.105 MPa Reference | 0.31965 | kg/m^3 | Reference [9]
mass NH3/hr | 1.0745 | kg/hr
Plant net power | 549.99 | MW | Reference [1]
mass NH3/MWh | 0.0019536 | kg/MWh
Calculating R for flue gas based on Exhibit 5-4 data
p=rho*R*T
R=p/(rho*T)
(
Air entering boiler (Streams 2)
Flue stream temperature | 19 | C | [1]
| 292.15 | K
Pressure | 0.11 | MPa | [1]
Rho (density) | 1.2 | kg/m^3 | [1]
R= | 0.00031377 | MPa/(kg/m^3*T)
Flue gas exiting boiler (Stream 10)
Flue stream temperature | 169 | C | [1]
| 442.15 | K
Pressure | 0.1 | MPa | [1]
Rho (density) | 0.8 | kg/m^3 | [1]
R= | 0.00028271 | MPa/(kg/m^3*T)
Average R | 0.00029824 | MPa/(kg/m^3*T)
SCR temperature is 260-455 C, Reference 1
Assuming P=0.10MPa
rho=p/(R*T)
R | 0.00029824 | MPa/(kg/m^3*T)
T | 400 | C | [1]
| 673.15 | K
p | 0.1 | MPa | [1]
rho | 0.49811 | kg/m^3
Assuming P=0.11MPa
rho=p/(R*T)
R | 0.00029824 | MPa/(kg/m^3*T)
T | 400 | C | [1]
| 673.15 | K
p | 0.11 | MPa | [1]
rho | 0.54792 | kg/m^3
Average density | 0.52302 | kg/m^3
With CCS
Calculation
volume NH3/10^6 volume flue gas | 1e-06 | m^3 NH3/m^3 flue
flue gas (stream 4 to stack) | 2428540 | kg/hr | (Exhibit 5-4 from Baseline Report, pg. 454)
flue gas density | 0.52302 | kg/m^3 | Density calculated below, between 0.1 and 0.11 MPa
flue gas volume flow rate | 4643337.4032 | m^3/hr
volume NH3/hr | 4.6433 | m^3/hr | based on 5pppmv
density NH3 @ 0.105 MPa | 0.31965 | kg/m^3 | [9]
mass NH3/hr | 1.4842 | kg/hr
Plant net power | 549.97 | MW | Reference [1]
mass NH3/MWh | 0.0026988 | MWh
Calculating R for flue gas based on Exhibit 5-4 data
p=rho*R*T
R=p/(rho*T)
(
Air entering boiler (Streams 2)
Flue stream temperature | 19 | C | [1]
| 292.15 | K
Pressure | 0.11 | MPa | [1]
Rho (density) | 1.2 | kg/m^3 | [1]
R= | 0.00031377 | MPa/(kg/m^3*T)
Flue gas exiting boiler (Stream 10)
Flue stream temperature | 169 | C | [1]
| 442.15 | K
Pressure | 0.1 | MPa | [1]
Rho (density) | 0.8 | kg/m^3 | [1] |  | Ammonia properties obtained from Reference 5
R= | 0.00028271 | MPa/(kg/m^3*T) |  |  | Temperature (K) | Pressure (MPa) | Density (kg/m3)
[5 empty] | 631.15 | 0.1 | 0.32473
Average R | 0.00029824 | MPa/(kg/m^3*T) |  |  | 631.15 | 0.105 | 0.34097
[5 empty] | 631.15 | 0.11 | 0.35722
SCR temperature is 260-455 C, Reference 1
[5 empty] | 673.15 | 0.1 | 0.30442
Assuming P=0.10MPa |  |  |  |  | 673.15 | 0.105 | 0.31965
rho=p/(R*T) |  |  |  |  | 673.15 | 0.11 | 0.33488
R | 0.00029824 | MPa/(kg/m^3*T)
T | 400 | C | [1]
| 673.15 | K
p | 0.1 | MPa | [1]
rho | 0.49811 | kg/m^3
673.15 0.10000 0.30442 3.2849 38.962 44.557 154.15 40.615 48.956 629.10 2.3395 24.405 0.076623 vapor
Assuming P=0.11MPa | [5 empty] | 673.15 0.10500 0.31965 3.1284 38.962 44.556 153.75 40.616 48.958 629.09 2.3394 24.406 0.076625 vapor
rho=p/(R*T) | [5 empty] | 673.15 0.11000 0.33488 2.9862 38.962 44.556 153.36 40.617 48.960 629.09 2.3393 24.406 0.076628 vapor
R | 0.00029824 | MPa/(kg/m^3*T)
T | 400 | C | [1]
| 673.15 | K
p | 0.11 | MPa | [1]
rho | 0.54792 | kg/m^3
Average density | 0.52302 | kg/m^3
Comparisons
Data for Oak Grove Power Plant - SCPC Plant using Lignite
Ammonia
2011 | 93337 | lb | From | http://oaspub.epa.gov/enviro/tris_control_v2.tris_print?tris_id=7785WKGRVS13MIL
hours/yr | 8766 | hrs
Capacity | 1600 | MW
Capacity factor | 0.85
Ammonia | 0.0078291 | lb/MWh
| 0.0035512 | kg/MWh
Ammonia
2010 | 46000 | lb
hours/yr | 8766 | hrs
Capacity | 1600 | MW
Capacity factor | 0.5
Ammonia | 0.0065594 | lb/MWh
| 0.0029753 | kg/MWh
Data for Gibson Generating Station - SCPC Plant using Bituminous
2011, 2010, 2009 | 956 | lb
hours/yr | 8766 | hrs
Capacity | 3145 | MW
Capacity factor | 0.85
Ammonia | 4.0796e-05 | lb/MWh
| 1.8505e-05 | kg/MWh

## Conversions
Conversions
Conversion Factors |  |  |  | References
1 | lb NG@STP | 23.8 | SCF NG | [2]
1 | kg | 2.2046 | lbm
1 | hr | 60 | minutes
1 | l | 0.26417 | gal
1 | MWh | 1000 | kWh
1 | year | 8766 | hours

## Assumptions
Assumptions
Assumption # | Description
1 | All of the sampled plants for lead emissions operated at 0.85 capacity factor
2 | Auxiliary boiler operates 50% of the time during plant shutdown periods
3 | Auxiliary boiler emissions are not captured
4 | Assume a 2 year life for SCR layers with an average slip rate of 1 ppmv