## Info
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
DS Sheet Information
|  | Process Name: | Operation of Existing Pulverized Coal Power Plant
|  | Process Description: | The operations of an existing pulverized coal (EXPC) power plant with or without carbon capture and sequestration (CCS) on the basis of 1MWh electricity output.
|  | Files: | This unit process is composed of this document and the file, Stage-3-O-EXPC_Power_Plant_baseline.docx, which provides additional details regarding calculations, data quality, and references as relevant.
|  | Summary and Calculations Worksheets: | As shown below, this document contains 3 summary worksheets (Data Summary, Reference Source Info, and DQI) that have been formatted consistent with NETL standards. The remaining 'calculations' worksheets are workspaces used by NETL engineers during the production of this unit process. The 'calculations' worksheets are presented for the convenience of the reader, and have not been subjected to standardized formatting.
This data sheet is organized as follows:
|  | Worksheet | Description
| Summary | Data Summary | Summary of Calculations, Input and Output Flows, Reference Flow, and other information
|  | Parameter Scenarios | Parameters for various scenarios where the unit process is used
|  | Reference Source Info | Referenced citations; citations are referenced by number, listed at the top of the Reference Source Info sheet
|  | DQI | Data Quality Index
| Calculations | eGRID-NEI data | Inputs and emissions from eGRID data
|  | Study Data-CO2 | CO2 emissions from baseline report data
|  | Conversions | Unit Conversions
|  | Assumptions | Assumptions
|  | GaBi Import | Data Summary page formatted for importation into the GaBi 4.4 software
How to Cite This Document:
This document should be cited as: NETL (2012). NETL Life Cycle Inventory Data – Unit Process: Operation of Existing Pulverized Coal Power Plant. U.S. Department of Energy, National Energy Technology Laboratory. Last Updated: September 2012 (version 01). www.netl.doe.gov/energy-analyses (http://www.netl.doe.gov/energy-analyses)
Additional Notes:
|  | For the calculations sheets, values |  | highlighted in yellow | are also pulled forward into the 'Data Summary' sheet
Bibliographic references & assumptions referenced by number; see 'Reference Source Info' & 'Assumptions' sheets for cross-reference.
Data Summary sheet color coding: white indicates data input by model engineer; blue indicates automatically calculated values
Abbreviations used throughout this DS: INSERT AS RELEVANT
Disclaimer:
Template Version:
1.0
Neither the U.S. Department of Energy (DOE) National Energy Technology Laboratory (NETL) nor any person acting on behalf of these organizations:
A. Makes any warranty or representation, express or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that the use of any information, apparatus, method, or process disclosed in this document may not infringe on privately owned rights; or
B. Assumes any liability with this report as to its use, or damages resulting from the use of any information, apparatus, method, or process disclosed in this document.
Reference herein to any specific commercial product, process, or service by trade name, trademark, manufacturer, or otherwise, does not necessarily constitute or imply its endorsement, recommendation, or favoring by NETL. The views and opinions of the authors expressed herein do not necessarily state or reflect those of NETL.

## Data Summary
NETL Life Cycle Inventory Data - Detailed Spreadsheet Documentation
Data Module Summary
Process Name: |  | Operation of Existing Pulverized Coal Power Plant
Reference Flow: |  | 1 | MWh | of | Electricity | [5 empty] | DQI | 1,2,3,1,1 | (see DQI sheet for explanation)
Brief Description: |  | The operations of an existing pulverized coal (EXPC) power plant with or without carbon capture and sequestration (CCS) on the basis of 1MWh electricity output.
SECTION I: META DATA
Geographical Coverage: |  | USA |  |  | Goal and Scope:
Region |  | Midwest |  |  | Reference Flow: 1 MWh of Electricity
Year Data Best Represents: |  | 2005
Process Type: |  | Energy Conversion (EC) |  |  | This unit process provides a summary of relevant input and output flows associated with the production of electricity by the combustion of coal in an existing (i.e., subcritical) pulverized coal power plant. This process can be used for scenarios with and without CCS. Key inputs include Illinois No. 6 coal and water from surface and ground sources. Key outputs include electricity, greenhouse gas emissions to air, and waste water.
Process Scope: |  | Gate-to-Gate Process (GG)
Allocation Applied: |  | No
Completeness: |  | Individual Relevant Flows Captured
Flows Aggregated in Data Set: |  |  |  |  | Note: All inputs and outputs are normalized per the reference flow (e.g., per MWh of electricity)
SECTION II: PARAMETERS
This section includes adjustable parameters, calculations needed to support adjustable parameters, and flow calculations based upon adjustable parameters.
| Parameter Name | Formula | Value | Min. Value | Max. Value | Unit | References | Comments
3 | CCS |  | 1 |  |  |  |  | [binary] If CO2 in flue gas is routed to CO2 recovery, value = 1. If CO2 in flue gas is released to atmosphere, value = 0.
12 | Net_MW_noCCS |  | 433.778 |  |  | MW | 1 | [MWh] Net Power Output for EXPC without CCS operation; Set value from retrofit study
10 | Net_MW_CCS |  | 303.317 |  |  | MW | 1 | [MWh] Net Power Output for EXPC with CCS operation; Set value from retrofit study
6 | Net_MW | IF(CCS=1;Net_MW_CCS;Net_MW_noCCS) | 303.317 |  |  | MWh |  | [MWh] Net Power Output for a single hour of IGCC operation with or without CCS, depending on value of "CCS" parameter
9 | Life_time |  | 30 |  |  | yrs |  | [Years] Life time of a power plant
9 | Plant_CCS | IF(CCS=1;1/(Life_time*365.25*24*Net_MW*0.85);0) | 1.4749e-08 |  |  | pce/MWh |  | [Piece/MWh] Fraction of a power plant per MWH. Capacity factor of 0.85
15 | EXPC_CO2caprate |  | 0.9 |  |  |  | 1 | [dimensionless] Fraction of CO2 captured
12 | EXPC_CO2_CCS |  | 134.5814 |  |  | kg/MWh | 3 | [kg/MWh] CO₂ emissions to air per MWh with CCS
14 | EXPC_CO2_noCCS |  | 941.0537 |  |  | kg/MWh | 3 | [kg/MWh] CO₂ emissions to air per MWh without CCS
8 | EXPC_CO2 | IF(CCS=1;EXPC_CO2_CCS;EXPC_CO2_noCCS) | 134.5814 |  |  | kg/MWh | 3 | [kg/MWh] CO₂ emissions to air per MWh without or without CCS, depending on value of "CCS" parameter
12 | EXPC_CO2_cap | IF(CCS=1;(EXPC_CO2*EXPC_CO2caprate/(1-EXPC_CO2caprate); 0) | 1211.233 |  |  | kg/MWh |  | [kg/MWh] CO₂ captured for CCS
12 | EXPC_NOx_CCS |  | 2.684 |  |  | kg/MWh | 3 | [kg/MWh] NOx emissions to air per MWh with CCS
14 | EXPC_NOx_noCCS |  | 1.8768 |  |  | kg/MWh | 3 | [kg/MWh] NOx emissions to air per MWh without CCS
8 | EXPC_NOx | IF(CCS=1;EXPC_NOx_CCS;EXPC_NOx_noCCS) | 2.684 |  |  | kg/MWh | 3 | [kg/MWh] NOx emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | EXPC_SO2_CCS |  | 3.171 |  |  | kg/MWh | 3 | [kg/MWh] SO₂ emissions to air per MWh with CCS
14 | EXPC_SO2_noCCS |  | 2.2173 |  |  | kg/MWh | 3 | [kg/MWh] SO₂ emissions to air per MWh without CCS
8 | EXPC_SO2 | IF(CCS=1;EXPC_SO2_CCS;EXPC_SO2_noCCS) | 3.171 |  |  | kg/MWh | 3 | [kg/MWh] SO₂ emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
| EXPC_PM25_CCS |  | 0.83892 |  |  | kg/MWh | 3,4 | [kg/MWh] Particulate matter (PM25) emissions to air per MWh with CCS
| EXPC_PM25_noCCS |  | 0.58661 |  |  | kg/MWh | 3,4 | [kg/MWh] Particulate matter (PM25) emissions to air per MWh without CCS
| EXPC_PM25 | IF(CCS=1;EXPC_PM25_CCS;EXPC_PM25_noCCS) | 0.83892 |  |  | kg/MWh | 3,4 | [kg/MWh] Particulate matter (PM25) emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
13 | EXPC_PM10_CCS |  | 0.89576 |  |  | kg/MWh | 3,4 | [kg/MWh] Particulate matter (PM10) emissions to air per MWh with CCS
15 | EXPC_PM10_noCCS |  | 0.62636 |  |  | kg/MWh | 3,4 | [kg/MWh] Particulate matter (PM10) emissions to air per MWh without CCS
9 | EXPC_PM10 | IF(CCS=1;EXPC_PM10_CCS;EXPC_PM10_noCCS) | 0.89576 |  |  | kg/MWh | 3,4 | [kg/MWh] Particulate matter (PM10) emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
11 | EXPC_Hg_CCS |  | 6.9215e-05 |  |  | kg/MWh | 3 | [kg/MWh] Mercury emissions to air per MWh with CCS
13 | EXPC_Hg_noCCS |  | 4.8398e-05 |  |  | kg/MWh | 3 | [kg/MWh] Mercury emissions to air per MWh without CCS
7 | EXPC_Hg | IF(CCS=1;EXPC_Hg_CCS;EXPC_Hg_noCCS) | 6.9215e-05 |  |  | kg/MWh | 3 | [kg/MWh] Mercury emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
11 | EXPC_Pb_CCS |  | 8.4118e-06 |  |  | kg/MWh | 3,4 | [kg/MWh] Lead emissions to air per MWh with CCS
13 | EXPC_Pb_noCCS |  | 5.8819e-06 |  |  | kg/MWh | 3,4 | [kg/MWh] Lead emissions to air per MWh without CCS
7 | EXPC_Pb | IF(CCS=1;EXPC_Pb_CCS;EXPC_Pb_noCCS) | 8.4118e-06 |  |  | kg/MWh | 3,4 | [kg/MWh] Lead emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | EXPC_NH3_CCS |  | 0.00029245 |  |  | kg/MWh | 3,4 | [kg/MWh] Ammonia emissions to air per MWh with CCS
14 | EXPC_NH3_noCCS |  | 0.00020449 |  |  | kg/MWh | 3,4 | [kg/MWh] Ammonia emissions to air per MWh without CCS
8 | EXPC_NH3 | IF(CCS=1;EXPC_NH3_CCS;EXPC_NH3_noCCS) | 0.00029245 |  |  | kg/MWh | 3,4 | [kg/MWh] Ammonia emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | EXPC_CH4_CCS |  | 0.01518 |  |  | kg/MWh | 3,4 | [kg/MWh] Methane emissions to air per MWh with CCS
14 | EXPC_CH4_noCCS |  | 0.010614 |  |  | kg/MWh | 3,4 | [kg/MWh] Methane emissions to air per MWh without CCS
8 | EXPC_CH4 | IF(CCS=1;EXPC_CH4_CCS;EXPC_CH4_noCCS) | 0.01518 |  |  | kg/MWh | 3,4 | [kg/MWh] Methane emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
11 | EXPC_CO_CCS |  | 0.14358 |  |  | kg/MWh | 3,4 | [kg/MWh] Carbon monoxide emissions to air per MWh with CCS
13 | EXPC_CO_noCCS |  | 0.10039 |  |  | kg/MWh | 3,4 | [kg/MWh] Carbon monoxide emissions to air per MWh without CCS
7 | EXPC_CO | IF(CCS=1;EXPC_CO_CCS;EXPC_CO_noCCS) | 0.14358 |  |  | kg/MWh | 3,4 | [kg/MWh] Carbon monoxide emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
12 | EXPC_VOC_CCS |  | 0.017341 |  |  | kg/MWh | 3,4 | [kg/MWh] Volatile organic compounds emissions to air per MWh with CCS
14 | EXPC_VOC_noCCS |  | 0.012126 |  |  | kg/MWh | 3,4 | [kg/MWh] Volatile organic compounds emissions to air per MWh without CCS
8 | EXPC_VOC | IF(CCS=1;EXPC_VOC_CCS;EXPC_VOC_noCCS) | 0.017341 |  |  | kg/MWh | 3,4 | [kg/MWh] Volatile organic compounds emissions to air per MWh with or without CCS, depending on value of "CCS" parameter
13 | EXPC_coal_CCS |  | 562.1933 |  |  | kg/MWh | 1,3 | [kg/MWh] Coal consumption per MWh with CCS
15 | EXPC_coal_noCCS |  | 393.1107 |  |  | kg/MWh | 1,3 | [kg/MWh] Coal consumption per MWh without CCS
9 | EXPC_coal | IF(CCS=1;EXPC_coal_CCS;EXPC_coal_noCCS) | 562.1933 |  |  | kg/MWh | 1,3 | [kg/MWh] Coal consumption per MWh with or without CCS, depending on value of "CCS" parameter
13 | EXPC_H2OinCCS |  | 306.9396 |  |  | L/MWh | 1,2 | [L/MWh] Water withdrawal with CCS
15 | EXPC_H2OinnoCCS |  | 175.3574 |  |  | L/MWh | 1,2 | [L/MWh] Water withdrawal without CCS
10 | EXPC_H2Oin | IF(CCS=1;EXPC_H2OinCCS;EXPC_H2OinnoCCS) | 306.9396 |  |  | L/MWh | 1,2 | [L/MWh] Water withdrawal with or without CCS, depending on value of "CCS" parameter
13 | EXPC_H2OinGnd | EXPC_H2Oin/2 | 153.4698 |  |  | L/MWh |  | [L/MWh] Ground water withdrawal
14 | EXPC_H2OinSurf | EXPC_H2Oin/2 | 153.4698 |  |  | L/MWh |  | [L/MWh] Surface water withdrawal
14 | EXPC_H2OoutCCS |  | 69.1285 |  |  | L/MWh | 2,5 | [L/MWh] Waste water with CCS
15 | EXPC_H2OoutnCCS |  | 39.4937 |  |  | L/MWh | 2 | [L/MWh] Waste water without CCS
11 | EXPC_H2Oout | IF(CCS=1;EXPC_H2OoutCCS;EXPC_H2OoutnCCS) | 69.1285 |  |  | L/MWh | 2,5 | [L/Mwh] Waster water with or without CCS, depending on value of "CCS"Parameter
8 | Repl_pwr | IF(CCS=1;0.430114369;0) | 0.43011 |  |  | MWh/MWh | 1 | [MWh/MWh] Electricity from grid to offset net power reduction from CCS
| End of List | <select this entire row, then insert new row>
SECTION III: INPUT FLOWS
This section includes all input flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
| Plant_CCS | CCS addition [Construction] | 1 | kg | 1.4749e-08 | pce/MWh | 1.4749e-08 | kg | X | Measured | 1,3 | [Technosphere] CCS addition to an existing plant
| EXPC_coal | Hard Coal (Illinois No 6) [Hard coal (resource)] | 1 | kg | 562.1933 | kg/MWh | 562.1933 | kg | X | Measured | 1,3 | [Technosphere] Coal for combustion
| Repl_pwr | Power (from grid mix) [System-dependent] | 1 | MWh | 0.43011 | MWh/MWh | 0.43011 | MWh | X | Calculated | 1 | [Technosphere] Electric power from grid to offset power diverted to CCS
| EXPC_H2OinGnd | Water (ground water) [Water] | 1 | L | 153.4698 | L/MWh | 153.4698 | L |  | Literature | 1,2 | [Resource] Ground water withdrawal
| EXPC_H2OinSurf | Water (surface water) [Water] | 1 | L | 153.4698 | L/MWh | 153.4698 | L |  | Literature | 1,2 | [Resource] Surface water withdrawal
| End of List | <select this entire row, then insert new row> | Factor |  |  |  | Amount |  |  | <select from list>
SECTION IV: OUTPUT FLOWS
This section includes all output flows considered for this unit process
| Parameter | Flow Name | Value | Units | Parameter | Unit | Total | Units per RF | Tracked | Origin | References | Comments
|  | Power [Electric Power] | 1 |  | 1 |  | 1 |  | X |  |  | Reference flow
| EXPC_CO2_cap | Carbon dioxide [Inorganic intermediate products] | 1 | kg | 1211.233 | kg/MWh | 1211.233 | kg | X | Calculated | 1 | CO₂ captured for CCS
| EXPC_CO2 | Carbon dioxide [Inorganic emissions to air] | 1 | kg | 134.5814 | kg/MWh | 134.5814 | kg |  | Measured | 3 | Emission to air
| EXPC_CH4 | Methane [Organic emissions to air (group VOC)] | 1 | kg | 0.01518 | kg/MWh | 0.01518 | kg |  | Measured | 3,4 | Emission to air
| EXPC_NOx | Nitrogen oxides [Inorganic emissions to air] | 1 | kg | 2.684 | kg/MWh | 2.684 | kg |  | Measured | 3 | Emission to air
| EXPC_SO2 | Sulphur dioxide [Inorganic emissions to air] | 1 | kg | 3.171 | kg/MWh | 3.171 | kg |  | Measured | 3 | Emission to air
| EXPC_CO | Carbon monoxide [Inorganic emissions to air] | 1 | kg | 0.14358 | kg/MWh | 0.14358 | kg |  | Measured | 3,4 | Emission to air
| EXPC_VOC | NMVOC (unspecified) [Group NMVOC to air] | 1 | kg | 0.017341 | kg/MWh | 0.017341 | kg |  | Measured | 3,4 | Emission to air
| EXPC_PM10 | Dust (PM10) [Particles to air] | 1 | kg | 0.89576 | kg/MWh | 0.89576 | kg |  | Measured | 3,4 | Emission to air
| EXPC_PM25 | Dust (PM2.5) [Particles to air] | 1 | kg | 0.83892 | kg/MWh | 0.83892 | kg |  | Measured | 3,4 | Emission to air
| EXPC_Pb | Lead (+II) [Heavy metals to air] | 1 | kg | 8.4118e-06 | kg/MWh | 8.4118e-06 | kg |  | Measured | 3,4 | Emission to air
| EXPC_Hg | Mercury (+II) [Heavy metals to air] | 1 | kg | 6.9215e-05 | kg/MWh | 6.9215e-05 | kg |  | Measured | 3 | Emission to air
| EXPC_NH3 | Ammonia [Inorganic emissions to air] | 1 | kg | 0.00029245 | kg/MWh | 0.00029245 | kg |  | Measured | 3,4 | Emission to air
| EXPC_H2Oout | Water (wastewater) [Water] | 1 | L | 69.1285 | L/MWh | 69.1285 | L |  | Literature | 2,5 | Renewable resources
| End of List | <select this entire row, then insert new row> | Factor | [6 empty] | <select from list>
Detailed Spreadsheet Lists
| Process Type | Process Scope | Completeness |  |  | Origin |  | Tracked
| <select from list> | <select from list> | <select from list> |  |  | <select from list>
| Extraction Process (EP) | Cradle-to-Grave (End-of-Life) Process (CE) | All Flows Captured |  |  | Measured |  | X
| Manufacturing Process (MP) | Cradle-to-Gate Process (CG) | All Relevant Flows Captured |  |  | Calculated |  | *
| Installation Process (IP) | Gate-to-Gate Process (GG) | Individual Relevant Flows Captured |  |  | Literature
| Basic Process (BP) | Gate-to-Grave (End-of-Life) Process (GE) | Some Relevant Flows Not Captured |  |  | Estimated
| Energy Conversion (EC) |  | No Statement |  |  | No Statement
Transport Process (TP)
Recovery Process (RP)
Waste Treatment Process (WT)
Auxiliary Process (AP)

## PS
Parameter Scenarios
| Parameter Name | Enter a Scenario ID below: | Scenario ID |  |  | [Units] Comments
|  | 3 | 1 | 2 | 3
|  | Operation of Existing Pulverized Coal Power Plant | Operation of Existing Pulverized Coal Power Plant
|  | Scenario 3 Name | Scenario 1 Name | Scenario 2 Name | Scenario 3 Name
| <Enter Parameters> | 0 |  |  |  | <Add comments from Data Summary Sheet>
| <for the Scenarios> | 0
0
0
0
0
0
Scenario Descriptions:
| Scenario ID | Description
| 1 | <Add detailed description to the Scenarios>
2
3
The purpose of this "Parameters Scenarios" worksheet is to provide a flexible method for adjusting parameters within this unit process. The above table allows you to select a scenario ID (CELL C4) and uses a lookup function to populate the adjustable parameters (the cells with yellow shading). The values for the adjustable parameters are linked to the "Data Summary" sheet.

## Reference Source Info
Field Name
Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
SourceType | Separate Publication | Separate Publication | Separate Publication | Separate Publication | Separate Publication
Title | Carbon Dioxide Capture from Existing Coal-Fired Power Plants | Power Plant Water Usage and Loss Study | eGrid2007 Year 2005 | 2005 National Emissions Inventory Data & Documentation; Point Facility Summary | Cost and Performance Baseline for Fossil Energy Plants, Volume 1: Bituminous Coal and Natural Gas to Electricity Report
FirstAuthor | NETL | NETL | EPA | EPA | NETL
AdditionalAuthors
Year | 2007 |  | 2009 | 2009 | 2010
Date | November 2007 |  | February 5, 2009 | January 2009
PlaceOfPublication | Pittsburgh, PA | Pittsburgh, PA
Publisher | National Energy Technology Laboratory | National Energy Technology Laboratory | Environmental Protection Agency | Environmental Protection Agency | National Energy Technology Laboratory
PageNumbers
Table or Figure Number
NameOfEditors
TitleOfAnthology
Journal
VolumeNo
IssueNo
Docket Number
Copyright
Internet Address | http://www.netl.doe.gov/energy-analyses/pubs/CO2%20Retrofit%20From%20Existing%20Plants%20Revised%20November%202007.pdf | http://www.netl.doe.gov/technologies/coalpower/gasification/pubs/pdf/WaterReport_Revised%20May2007.pdf | http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html | http://www.epa.gov/ttn/chief/net/2005inventory.html | http://www.netl.doe.gov/energy-analyses/pubs/BitBase_FinRep_Rev2.pdf
Internet Access Date | August 20, 2012 | August 20, 2012 | August 20, 2012 | August 20, 2012 | August 20, 2012
Data Type (Origin) | Literature | Literature | Measured | Measured | Literature
Year Data Represents | 2007 | 2007 | 2005 |  | 2010
Geographical Representation | Midwest, USA | Chicago, IL | USA | USA | Midwest
Representativeness | One facility |  | Multiple Facilities | Multiple Facilities
BibliographicText | NETL, 2007. Carbon Dioxide Capture from Existing Coal-Fired Power Plants, National Energy Technology Laboratory, Pittsburgh, PA. Accessed on August 20, 2012 at http://www.netl.doe.gov/energy-analyses/pubs/CO2%20Retrofit%20From%20Existing%20Plants%20Revised%20November%202007.pdf. | NETL, . Power Plant Water Usage and Loss Study, National Energy Technology Laboratory, Pittsburgh, PA. Accessed on August 20, 2012 at http://www.netl.doe.gov/technologies/coalpower/gasification/pubs/pdf/WaterReport_Revised%20May2007.pdf. | EPA, 2009. eGrid2007 Year 2005, Environmental Protection Agency, . Accessed on August 20, 2012 at http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html. | EPA, 2009. 2005 National Emissions Inventory Data & Documentation; Point Facility Summary, Environmental Protection Agency, . Accessed on August 20, 2012 at http://www.epa.gov/ttn/chief/net/2005inventory.html. | NETL, 2010. Cost and Performance Baseline for Fossil Energy Plants, Volume 1: Bituminous Coal and Natural Gas to Electricity Report, National Energy Technology Laboratory, . Accessed on August 20, 2012 at http://www.netl.doe.gov/energy-analyses/pubs/BitBase_FinRep_Rev2.pdf.
Text/Description | Tables ES-1, ES-3, 3-1
Reference Source Info Lists
Source Type
<select from list>
Undefined
Article
Chapters in Anthology
Separate Publication
Measurement on Site
Oral Communication
Personal Written Communication
Questionnaires

## DQI
Data Quality Index
DQI Determination
| Input/Output | Reference (see 'Reference Source Info' worksheet) | Source Reliability | Completeness | Temporal Correlation | Geographical Correlation | Technical Correlation | DQI | Recommendations | Determinations
| Coal | 1,3 | 1 | 1 | 2 | 1 | 1 | 1,1,2,1,1 | Requirements met | OK
| Replacement Power | 1 | 1 | 2 | 2 | 1 | 1 | 1,2,2,1,1
| Surface water | 1,2 | 1 | 2 | 2 | 1 | 1 | 1,2,2,1,1
| Ground water | 1,2 | 1 | 2 | 2 | 1 | 1 | 1,2,2,1,1
| CO₂ | 3 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| CH₄ | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| NOx | 3 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| SO₂ | 3 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| CO | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| VOC | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| PM10 | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| PM25 | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| Pb | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| Hg | 3 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1
| NH₃ | 3,4 | 1 | 2 | 3 | 1 | 1 | 1,2,3,1,1 | Requirements met | OK
| Water discharge | 2,5 | 1 | 2 | 2 | 1 | 1 | 1,2,2,1,1 | Requirements met | OK
| Total | [6 empty] | 1,2,3,1,1
DQI Methodology
DQI Matrix (from NETL LCI&C Guideline Document, adapted from Weidema and Wenaes)
| Indicator | Score
|  | 1 | 2 | 3 | 4 | 5
| Source Reliability (for most applications, source quality guidelines only factor) | data verified based on measurements | data verified based on some assumptions and/or standard science and engineering calculations | data verified with many assumptions, or non-verified but from quality source | qualified estimate | non-qualified estimate
|  | source quality guidelines met |  | source quality guidelines not met
|  | data cross checks, greater than or equal to 3 quality sources | 2 or less data sources available for cross check, or data sources available that do not meet quality standards |  | no data available for cross check
| Completeness | representative data from a sufficient sample of sites over an adequate period of time | smaller number of site but an adequate period of time | sufficient number of sites but a less adequate period of time | smaller number of sites and shorter periods or incomplete data from an adequate number of sites or periods | representativeness unknown or incomplete data sets
| Temporal Correlation | less than three years of difference to year of study/current year | less than 6 years of difference | less than 10 years difference | less than 15 years difference | age of data unknown or more than 15 years difference
| Geographical Correlation | data from area under study | average data from larger area or specific data from a close area | data from area with similar production conditions | data from area with slightly similar production conditions | data from unknown area or area with very different production conditions
| Technological Correlation | data from technology, process or materials being studied | data from a different technology using the same process and/or materials |  | data on related process or material using the same technology | data or related process or material using a different technology
Indicator Descriptions
Source Reliability -- This indicator relates to the quality of the data source and the verification of the data collection methods used within the source.
Data Verification -- Source data that have been verified within error bounds by either the source author (with a high level of transparency) or the LCI modeler. Verification can be done by measurement, including on-site checking, recalculation, or mass or energy balance analysis. If the source data cannot be verified without making assumptions (i.e., not enough data are available to close the mass/energy balance), then the score should be a 2 or 3, depending on the number of assumptions. If no source data are available, a qualified estimate from an expert in the field should receive a score of 4, and an estimate from a non-expert should receive a score of 5. Mostly applicable to primary data.
Source Quality Guidelines -- The highest quality source should be
o From a peer reviewed journal or a government sponsored study. If the source is an LCA, it must meet ISO requirements.
o Publicly available either for free or at cost, or directly representative of the process of interest.
o Written/published by an unbiased party.
o An unbiased survey of experts or process locations.
When the source used for data is a reputable model that does not specifically meet the above criteria, it is the discretion of the modeler to determine the rank of the source. An example for justification would be if the data have been used in published reports that met the data quality standards.
Data Cross-Check -- The number of sources that verify the same data point or series, within reason. As a general benchmark, a high standard is greater than or equal to three data cross checks with quality approved sources. This typically refers to primary data, and if no other data sources are available, this can be omitted.
Completeness -- This indicator quantifies the statistical robustness of the source data. This ranking is based on how many data points were taken, how representative the sample is to the studied process, and whether the data were taken for an acceptable time period to even out normal process fluctuations. The following examples are given to help clarify this indicator.
Temporal Correlation -- This indicator represents how well the time period in which the data were collected corresponds with the year of the study. If the study is set to evaluate the use of a technology from 2000 to 2040, data from 1970 would not be very accurate. It is important when assigning this ranking to take notice of any discrepancies between the year the source was published and the year(s) the data were collected.
Geographical Correlation -- This indicator represents the appropriateness between the region of study and the source data region. This indicator becomes important when comparing data from different countries. For example, technological advances might reasonably be expected to develop differently in different countries, so efficiency and energy use might be very different. This is also important when looking at best management practices for carbon mitigation.
Technological Correlation -- This indicator embodies all other differences that may be present between the study goals and the data source. From the above example, using data for a type of biomass that is not being studied in the LCA should result in a lower technological representativeness ranking.
Steps for Applying DQM
1) Calculate score for each unit process (UP) input. If more than one reference source is used for one input, and the score is lower, consider both scores. If an indicator does not relate to a specific source, assume N/A. If all emissions come from one source, only one score is needed
- when a score is determined for a particular reference source, add to 'Reference Source Info' for future use
2) From the reference scores, determine the data quality indicator (DQI) for the unit process inputs for commissioning/decommissioning operations (when applicable)*
- the scores are not additive, rather, the lowest score for an indicator of a particular data input is the lowest score for the UP
3) Significant inputs of low quality unit processes (DQI mostly 3-5) should be varied to the minimum and maximum values or 95 percent confidence interval of the uncertainty range.
- check significance first. If the input is not significant by a long shot (or with the maximum possible value), it is not necessary to include in the UP
4) If the change in the final result from a single unit process is greater than a threshold value, for example, 0.1 g CO2e/MJ, then the processes should be flagged for possible additional data quality refinement
- for example, if emissions from the total steel inputs are found to be significant during sensitivity, the DQI will be performed on the steel profile. If this is not possible (because data are not transparent/purchased), it will be listed as a future recommendation
- if, however, the steel inputs are significant due to a large amount of steel needed for a particular process, then the DQI on that input should be performed and the data refined if needed
5) If the UP input is significant (with or without sensitivity), but no data refinement is possible, this is listed as a data limitation and noted in the report
* For NETL LCI&C studies, because data quality for construction is typically low, sensitivity on those inputs is already performed and the DQI does not need to be calculated. If sensitivity is not performed on construction, or sensitivity shows that a particular input is significant, then the DQI will be performed

## eGRID-NEI data
CALCULATION OF INPUTS and EMISSIONS
eGRID2007 (2005 data for Conesville power plant) Reference [3]
eGRID2007 2005 file plant sequence number | State abbreviation | Plant name | DOE/EIA ORIS plant or facility code | Plant EPA Facility Registry System (FRS) identification code | Plant operator name | Plant operator ID | Utility service area name | Utility service area ID | Parent company ID associated with the operator | Parent company name associated with the operator | Power control area name | Power control area ID | NERC region acronym | eGRID subregion acronym | eGRID subregion name | Plant FIPS State code | Plant FIPS county code | Plant county name | Plant latitude | Plant longitude | County centroid flag: 1 = county centroid used | Number of boilers | Number of generators | Plant combustion status | Plant emissions source(s) | Plant primary fuel | Plant primary coal/oil/gas/ other fossil fuel category | Flag indicating if the plant used any amount of coal: 1 = Yes | Plant capacity factor | Plant nameplate capacity (MW) | Renewable methane/ biomass plant adjustment flag | Combined heat and power (CHP) plant adjustment flag: 1 = Yes | CHP plant useful thermal output (MMBtu) | CHP plant power to heat ratio | CHP plant electric allocation factor | Plant pumped storage flag: 1 = Yes | Plant annual heat input (MMBtu) | Plant ozone season heat input (MMBtu) | Plant annual net generation (MWh) | Plant ozone season net generation (MWh) | Plant annual NOx emissions (tons) | Plant ozone season NOx emissions (tons) | Plant annual SO2 emissions (tons) | Plant annual CO2 emissions (tons) | Plant annual CH4 emissions (lbs) | Plant annual N2O emissions (lbs) | Plant annual Hg emissions (lbs) | Plant annual NOx output emission rate (lb/MWh) | Plant ozone season NOx output emission rate (lb/MWh) | Plant annual SO2 output emission rate (lb/MWh) | Plant annual CO2 output emission rate (lb/MWh) | Plant annual CH4 output emission rate (lb/GWh) | Plant annual N2O output emission rate (lb/GWh) | Plant annual Hg output emission rate (lb/GWh) | Plant annual NOx input emission rate (lb/MMBtu) | Plant ozone season NOx input emission rate (lb/MMBtu) | Plant annual SO2 input emission rate (lb/MMBtu) | Plant annual CO2 input emission rate (lb/MMBtu) | Plant annual Hg input emission rate (lb/BBtu) | Plant annual NOx combustion output emission rate (lb/MWh) | Plant ozone season NOx combustion output emission rate (lb/MWh) | Plant annual SO2 combustion output emission rate (lb/MWh) | Plant annual CO2 combustion output emission rate (lb/MWh) | Plant annual CH4 combustion output emission rate (lb/GWh) | Plant annual N2O combustion output emission rate (lb/GWh) | Plant annual Hg combustion output emission rate (lb/GWh) | Plant unadjusted annual NOx emissions (tons) | Plant unadjusted ozone season NOx emissions (tons) | Plant unadjusted annual SO2 emissions (tons) | Plant unadjusted annual CO2 emissions (tons) | Plant unadjusted annual CH4 emissions (lbs) | Plant unadjusted annual N2O emissions (lbs) | Plant unadjusted annual Hg emissions (lbs) | Plant unadjusted annual heat input (MMBtu) | Plant unadjusted ozone season heat input (MMBtu) | Plant nominal heat rate (Btu/kWh) | Plant annual coal net generation (MWh) | Plant annual oil net generation (MWh) | Plant annual gas net generation (MWh) | Plant annual nuclear net generation (MWh) | Plant annual hydro net generation (MWh) | Plant annual biomass net generation (MWh) | Plant annual wind net generation (MWh) | Plant annual solar net generation (MWh) | Plant annual geothermal net generation (MWh) | Plant annual other fossil net generation (MWh) | Plant annual other unknown/ purchased fuel net generation (MWh) | Plant annual total nonrenewables net generation (MWh) | Plant annual total renewables net generation (MWh) | Plant annual total nonhydro renewables net generation (MWh) | Plant annual total combustion net generation (MWh) | Plant annual total noncombustion net generation (MWh) | Plant coal generation percent (resource mix) | Plant oil generation percent (resource mix) | Plant gas generation percent (resource mix) | Plant nuclear generation percent (resource mix) | Plant hydro generation percent (resource mix) | Plant biomass generation percent (resource mix) | Plant wind generation percent (resource mix) | Plant solar generation percent (resource mix) | Plant geothermal generation percent (resource mix) | Plant other fossil generation percent (resource mix) | Plant other unknown / purchased fuel generation percent (resource mix) | Plant total nonrenewables generation percent (resource mix) | Plant total renewables generation percent (resource mix) | Plant total nonhydro renewables generation percent (resource mix) | Plant total combustion generation percent (resource mix) | Plant total noncombustion generation percent (resource mix) | Plant owner name (first) | Plant owner code (first) | Plant owner percent (first) | Plant owner name (second) | Plant owner code (second) | Plant owner percent (second) | Plant owner name (third) | Plant owner code (third) | Plant owner percent (third) | Plant owner name (fourth) | Plant owner code (fourth) | Plant owner percent (fourth) | Plant owner name (fifth) | Plant owner code (fifth) | Plant owner percent (fifth) | Plant owner name (sixth) | Plant owner code (sixth) | Plant owner percent (sixth) | Plant owner name (seventh) | Plant owner code (seventh) | Plant owner percent (seventh) | Plant owner name (eighth) | Plant owner code (eighth) | Plant owner percent (eighth) | Plant owner name (ninth) | Plant owner code (ninth) | Plant owner percent (ninth) | Plant owner name (tenth) | Plant owner code (tenth) | Plant owner percent (tenth) | Plant owner name (eleventh) | Plant owner code (eleventh) | Plant owner percent (eleventh) | Plant owner name (twelfth) | Plant owner code (twelfth) | Plant owner percent (twelfth) | Plant owner name (thirteenth) | Plant owner code (thirteenth) | Plant owner percent (thirteenth) | Plant owner name (fourteenth) | Plant owner code (fourteenth) | Plant owner percent (fourteenth) | Plant owner name (fifteenth) | Plant owner code (fifteenth) | Plant owner percent (fifteenth) | Plant owner name (sixteenth) | Plant owner code (sixteenth) | Plant owner percent (sixteenth) | eGRID2006 2004 file plant sequence number
3638 | OH | Conesville | 2840 | 110000605417 | Columbus Southern Power Co | 4062 |  | 0 | -7303 | American Electric Power Co | PJM Interconnection | 14725 | RFC | RFCW | RFC West | 39 | 031 | Coshocton | 40.1842 | -81.8811 | 0 | 6 | 6 | 1 | CEM, ICR | BIT | COAL | 1 | 0.51 | 2174.8 | 0 | 0 | 0 | 0 | 0 | 0 | 97755269 | 36004152 | 9716702 | 3534038 | 21158.405 | 5120.122 | 106628.501 | 10029697.9 | 227378.756 | 341068.133 | 1036.4772 | 4.3551 | 2.8976 | 21.9475 | 2064.4243 | 23.4008 | 35.1012 | 0.1067 | 0.4329 | 0.2844 | 2.1815 | 205.2001 | 0.0106 | 4.3551 | 2.8976 | 21.9475 | 2064.4243 | 23.4008 | 35.1012 | 0.1067 | 21158.405 | 5120.122 | 106628.501 | 10029697.9 | 227378.756 | 341068.133 | 1036.4772 | 97755269 | 36004152 | 10060.54 | 9705537 | 11165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9716702 | 0 | 0 | 9716702 | 0 | 99.8851 | 0.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | Duke Ohio Inc | 3542 | 15.4773 | Columbus Southern Power Co | 4062 | 78.1383 | Dayton Power & Light Co | 4922 | 6.3844 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 3519
eGRID2007 2005 file generator sequence number | State abbreviation | Plant name | DOE/EIA ORIS plant or facility code | Generator ID | Number of associated boilers | Generator status | Prime mover type | Primary generator fuel | Generator nameplate capacity (MW) | Generator capacity factor | Generator annual net generation (MWh) | Generator ozone season net generation (MWh) | Generation data source | Generator year on-line
11801 | OH | Conesville | 2840 | 1 | 1 | RE | ST | BIT | 148 | 0.032 | 41534 | 0 | 767 | 1959
11802 | OH | Conesville | 2840 | 2 | 1 | RE | ST | BIT | 136 | 0.0573 | 68262 | 0 | 767 | 1957
11803 | OH | Conesville | 2840 | 3 | 1 | OP | ST | BIT | 161.5 | 0.5137 | 726694 | 301468 | 767 | 1962
11804 | OH | Conesville | 2840 | 4 | 1 | OP | ST | BIT | 841.5 | 0.603 | 4444719 | 1606995 | 767 | 1973
11805 | OH | Conesville | 2840 | 5 | 1 | OP | ST | BIT | 443.9 | 0.6242 | 2427313 | 941177 | 767 | 1976
11806 | OH | Conesville | 2840 | 6 | 1 | OP | ST | BIT | 443.9 | 0.5344 | 2078020 | 729398 | 767 | 1978
eGRID2007 2005 file boiler sequence number | State abbreviation | Plant name | DOE/EIA ORIS plant or facility code | Boiler ID | Acid Rain Program flag: 1 = Yes | NOx Budget Program flag: 1 = Yes | Boiler bottom and firing types | Number of associated generators | Primary boiler fuel | Hours connected to load | Boiler unadjusted annual ETS/CEM heat input (MMBtu) | Boiler unadjusted ozone season ETS/CEM heat input (MMBtu) | Boiler unadjusted annual total EIA-based calculated heat input (MMBtu) | Boiler unadjusted ozone season EIA-based calculated heat input (MMBtu) | Boiler unadjusted annual ETS/CEM NOx emissions (tons) | Boiler unadjusted ozone season ETS/CEM NOx emissions (tons) | Boiler unadjusted annual EIA-based calculated NOx emissions (tons) | Boiler unadjusted ozone season EIA-based calculated NOx emissions (tons) | Boiler unadjusted annual ETS/CEM SO2 emissions (tons) | Boiler unadjusted annual EIA-based calculated SO2 emissions (tons) | Boiler unadjusted annual ETS/CEM CO2 emissions (tons) | Boiler unadjusted annual EIA-based calculated CO2 emissions (tons) | Source of "best" data from ETS/CEM or EIA-767 | Boiler unadjusted annual best heat input (MMBtu) | Boiler unadjusted ozone season best heat input (MMBtu) | Boiler unadjusted annual best NOx emissions (tons) | Boiler unadjusted ozone season best NOx emissions (tons) | Boiler unadjusted annual best SO2 emissions (tons) | Boiler unadjusted annual best CO2 emissions (tons) | SO2 (scrubber) first control device | NOx first control device | Hg Activated carbon injection system flag: 1 = Yes | Boiler year on-line
3312 | OH | Conesville | 2840 | 1 | 1 | 1 | CYCL | 1 | BIT | 0 | 372526 | 0 | 0 | 0 | 172.647 | 0 | 0 | 0 | 681.061 | 0 | 38220.79 | 0 | ETS/CEM | 372526 | 0 | 172.647 | 0 | 681.061 | 38220.79 |  |  | 0 | 1959
3313 | OH | Conesville | 2840 | 2 | 1 | 1 | CYCL | 1 | BIT | 0 | 663198 | 0 | 0 | 0 | 297.405 | 0 | 0 | 0 | 1220.478 | 0 | 68043.335 | 0 | ETS/CEM | 663198 | 0 | 297.405 | 0 | 1220.478 | 68043.335 |  |  | 0 | 1957
3314 | OH | Conesville | 2840 | 3 | 1 | 1 | DRY WALL | 1 | BIT | 0 | 7301033 | 3126814 | 0 | 0 | 1841.749 | 648.974 | 0 | 0 | 13141.924 | 0 | 749089.675 | 0 | ETS/CEM | 7301033 | 3126814 | 1841.749 | 648.974 | 13141.924 | 749089.675 |  | LNB | 0 | 1962
3315 | OH | Conesville | 2840 | 4 | 1 | 1 | TANG | 1 | BIT | 0 | 44779193 | 16643140 | 0 | 0 | 9580.224 | 2192.229 | 0 | 0 | 80980.932 | 0 | 4594348.125 | 0 | ETS/CEM | 44779193 | 16643140 | 9580.224 | 2192.229 | 80980.932 | 4594348.125 |  |  | 0 | 1973
3316 | OH | Conesville | 2840 | 5 | 1 | 1 | TANG | 1 | BIT | 0 | 24541261 | 9552287 | 0 | 0 | 4979.07 | 1323.905 | 0 | 0 | 5932.66 | 0 | 2517934.749 | 0 | ETS/CEM | 24541261 | 9552287 | 4979.07 | 1323.905 | 5932.66 | 2517934.749 | WL FGD |  | 0 | 1976
3317 | OH | Conesville | 2840 | 6 | 1 | 1 | TANG | 1 | BIT | 0 | 20098058 | 6681911 | 0 | 0 | 4287.31 | 955.014 | 0 | 0 | 4671.446 | 0 | 2062061.226 | 0 | ETS/CEM | 20098058 | 6681911 | 4287.31 | 955.014 | 4671.446 | 2062061.226 | WL FGD |  | 0 | 1978
NEI (2005 data for Conesville power plant) Reference [4]
Tribal Code | Tribal Name | State & County FIPS | State Abbreviation | County Name | Facility Site ID | NEI Site ID | Facility Name | Site Description | Address | City | ST | NAICS Code | NAICS Description | SIC | SIC Description | Lattitude | Longitude | NUM_CAPS | CAP_TONS | NUM_HAPS | HAP_TONS | SO2 | NOX | VOC | CO | PM10-PRI | PM10-FIL | PM25-PRI | PM25-FIL | PM-CON | NH3 | Hydrochloric Acid (Hydrogen Chloride (Gas Only)) | Hydrogen Fluoride (Hydrofluoric Acid) | Chlorine | Polychlorinated Biphenyls (Aroclors) | Mercury Compounds | Lead Compounds | Nickel Compounds | Manganese Compounds | Cadmium Compounds | Chromium Compounds | Beryllium Compounds | Antimony Compounds | Cobalt Compounds | Selenium Compounds | Arsenic Compounds(Inorganic Including Arsine) | Cyanide Compounds | Coke Oven Emissions | Naphthalene | Polycyclic Organic Matter as 15-PAH | Polycyclic Organic Matter as 7-PAH | Polycyclic Organic Matter as non-15 PAH | Acrolein | 1,3-Butadiene | Benzene (Including Benzene From Gasoline) | Toluene | Xylenes (Mixed Isomers) | 1,1,2,2-Tetrachloroethane | Tetrachloroethylene (Perchloroethylene) | 1,1,2-Trichloroethane | Methyl Chloroform (1,1,1-Trichloroethane) | Carbon Tetrachloride | Chloroform | Methylene Chloride (Dichloromethane) | Trichloroethylene | 1,3-Dichloropropene | Ethylene Dichloride (1,2-Dichloroethane) | Ethylene Dibromide (Dibromoethane) | Propylene Dichloride (1,2-Dichloropropane) | Vinyl Chloride | 2,4-Toluene Diisocyanate | Benzidine | Ethylene Oxide | Hexachlorobenzene | Hexamethylene Diisocyanate | Hydrazine | Quinoline | Triethylamine | Acetaldehyde | Formaldehyde | Propionaldehyde | Ethyl Acrylate | Acrylic Acid | Acrylonitrile | Isophorone | Maleic Anhydride | Methanol | Methyl Ethyl Ketone (2-Butanone) | Methyl Isobutyl Ketone (Hexone) | Methyl Methacrylate | Styrene | Ethylene Glycol | 1,1-Dimethylhydrazine | 1,2,3,4,5,6-Hexachlorocyclyhexane(stereo isomers) | 1,2,4-Trichlorobenzene | 1,2-Dibromo-3-Chloropropane | 1,2-Diphenylhydrazine | 1,2-Epoxybutane | 1,2-Propylenimine (2-Methylaziridine) | 1,3-Propane Sultone | 1,4-Dichlorobenzene | 2,2,4-Trimethylpentane | 2,4,5-Trichlorophenol | 2,4,6-Trichlorophenol | 2,4-D (Dichlorophenoxyacetic Acid)(Including Salts And Esters) | 2,4-Dinitrophenol | 2,4-Dinitrotoluene | 2-Acetylaminofluorene | 2-Chloroacetophenone | 2-Nitropropane | 3,3'-Dichlorobenzidene | 3,3'-Dimethoxybenzidine | 3,3'-Dimethylbenzidine | 4,4'-Methylenebis(2-Chloroaniline) | 4,4'-Methylenedianiline | 4,4'-Methylenediphenyl Diisocyanate (MDI) | 4,6-Dinitro-o-Cresol (Including Salts) | 4-Aminobiphenyl | 4-Dimethylaminoazobenzene | 4-Nitrobiphenyl | 4-Nitrophenol | Acetamide | Acetonitrile | Acetophenone | Acrylamide | Allyl Chloride | Aniline | Asbestos | Benzotrichloride | Benzyl Chloride | Beta-Propiolactone | Biphenyl | Bis(2-Ethylhexyl)Phthalate (Dehp) | Bis(Chloromethyl) Ether | Bromoform | Calcium Cyanamide | Captan | Carbaryl | Carbon Disulfide | Carbonyl Sulfide | Catechol | Chloramben | Chlordane | Chloroacetic Acid | Chlorobenzene | Chlorobenzilate | Chloromethyl Methyl Ether | Chloroprene | Cresol/Cresylic Acid (Mixed Isomers) | Cumene | Dde (1,1-Dichloro-2,2-Bis(p- Chlorophenyl) Ethylene) | Diazomethane | Dibenzofuran | Dibutyl Phthalate | Dichloroethyl Ether (Bis{2-Chloroethyl)Ether) | Dichlorvos | Diethanolamine | Diethyl Sulfate | Dimethyl Phthalate | Dimethyl Sulfate | Dimethylcarbamoyl Chloride | Epichlorohydrin (1-Chloro-2,3-Epoxypropane) | Ethyl Carbamate (Urethane) Chloride (Chloroethane) | Ethyl Chloride | Ethylbenzene | Ethylene Thiourea | Ethyleneimine (Aziridine) | Ethylidene Dichloride (1,1-Dichloroethane) | Fine Mineral Fibers | Glycol Ethers | Heptachlor | Hexachlorobutadiene | Hexachlorocyclopentadiene | Hexachloroethane | Hexamethylphosphoramide | Hexane | Hydroquinone | Methoxychlor | Methyl Bromide (Bromomethane) | Methyl Chloride (Chloromethane) | Methyl Iodide (Iodomethane) | Methyl Isocyanate | Methyl Tert-Butyl Ether | Methylhydrazine | N,N-Dimethylaniline | N,N-Dimethylformamide | Nitrobenzene | N-Nitrosodimethylamine | N-Nitrosomorpholine | N-Nitroso-N-Methylurea | o-Anisidine | o-Toluidine | Parathion | p-Dioxane | Pentachloronitrobenzene (Qunumeric(38,28)obenzene) | Pentachlorophenol | Phenol | Phosgene | Phosphine | Phosphorus | Phthalic Anhydride | p-Phenylenediamine | Propoxur (Baygon) | Propylene Oxide | Quinone (p-Benzoquinone) | Radionuclides (Including Radon) | Styrene Oxide | Titanium Tetrachloride | Toluene-2,4-Diamine | Toxaphene (Chlorinated Camphene) | Trifluralin | Vinyl Acetate | Vinyl Bromide | Vinylidene Chloride (1,1-Dichloroethylene) | PM-FIL | PM-PRI
000 | Non-tribal | 39031 | OH | COSHOCTON CO | 0616000000 | NEI7865 | CONESVILLE POWER PLA | Southeast District Office | 47201 COUNTY ROAD 273 | Conesville | OH | 221112 | Fossil Fuel Electric Power Generation | 4911 | Electric, Gas And Sanitary Services Electric Services Electric Services | 40.18336 | -81.87781 | 123 | 148989.0601 | 403 | 248.0669 | 106585.9168 | 21158.8051 | 129.8772 | 1075.3127 | 6708.8232 | 730.4912 | 6283.0518 | 324.7697 | 5954.762 | 2.1903 | 216.1245 | 27.0155 |  |  | 0.47814 | 0.063 | 0.050562 | 0.088517 | 0.0093185 | 0.04696 | 0.0039154 | 0.0032419 | 0.01801 | 0.2348 | 0.07402 | 0.45026 |  | 0.0025062 | 0.0011454 | 0.0090844 | 3.9623e-06 | 0.052243 | 0.0007104 | 0.23548 | 0.04369 | 0.006983 |  | 0.0077445 |  |  |  | 0.010626 | 0.05223 |  |  | 0.086372 | 0.0072042 | [10 empty] | 0.10425 | 0.054011 | 0.82054 |  |  |  | 0.10446 |  |  |  |  | 0.0036021 | 0.0045026 | [15 empty] | 5.0429e-05 |  | 0.0012607 | [14 empty] | 0.0027016 | [5 empty] | 0.12607 |  | 0.00030618 | 0.013148 |  | 0.0070241 |  |  |  | 0.023414 | [5 empty] | 0.047505 |  |  |  |  | 0.00095455 | [9 empty] | 0.008645 |  |  |  | 0.0075644 | 0.01693 | [10 empty] | 0.012067 |  |  | 0.34549 | 1.1444 |  |  | 0.0063036 | 0.030618 | [12 empty] | 0.0028817 | [14 empty] | 0.0013688 |  |  |  | 35.06
Modeling of unit operations does not mirror actual operations for the facility/unit in question. Modeling assumes an 85% capacity factor while the actual capacity factor is 62.4%
Emissions rates are adjusted/scaled to the 90% net output by ratioing the net plant power for the base case to the 90% capture case and is noted as a data limitation.
|  |  |  | Base Case | 90% Capture |  | Increase in Emissions rates Due to CCS (per unit)
Net Plant Power (kW) |  |  |  | 433778 | 303317 |  |  | 1.4301
|  |  | Carbon Dioxide - Captured |  | 1211.233 | kg/MWh | Data specific to Unit #5; Derived from eGRID data; 90% capture of CO2 | [5 empty] | Used for CO2 leakage calculations
Species:
Carbon Dioxide - Inorganic Emission to Air |  |  |  | 941.0537 | 134.5814 | kg/MWh | Data specific to Unit #5; Derived from eGRID data; 90% capture of CO2
VOCs - unspecified |  |  |  | 0.012126 | 0.017341 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from NEI data
Methane - Organic Emissions to Air |  |  |  | 0.010614 | 0.01518 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from eGRID data
Nitrogen Oxides - Inorganic Emissions to Air |  |  |  | 1.8609 | 2.6613 | kg/MWh | Data specific to Unit #5; Derived from eGRID data
Nitrous oxide - Inorganic Emissions to Air |  |  |  | 0.015922 | 0.02277 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from eGRID data
Sulfur Dioxide (SO2) - Inorganic Emissions to Air |  |  |  | 2.2173 | 3.171 | kg/MWh | Data specific to Unit #5; Derived from eGRID data
Particulate Matter PM25 - Particles to Air |  |  |  | 0.58661 | 0.83892 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from NEI data
Particulate Matter PM10 - Particles to Air |  |  |  | 0.62636 | 0.89576 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from NEI data
Carbon Monoxide - Inorganic Emissions to Air |  |  |  | 0.10039 | 0.14358 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from NEI data
Lead - Heavy Metals to Air |  |  |  | 5.8819e-06 | 8.4118e-06 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from NEI data
Mercury - Heavy Metals to Air |  |  |  | 4.8398e-05 | 6.9215e-05 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from eGRID data
Ammonia to air |  |  |  | 0.00020449 | 0.00029245 | kg/MWh | Data for the entire power plant (comprised of six units); Derived from NEI data
From eGRID Data:
Coal Input |  |  |  | 10.1105 | 14.4591 | MMBtu/MWh |  | Data specific to Unit #5; Derived from eGRID data
Study Coal Input |  |  |  | 406.0949 | 580.7621 | kg/MWh |  | See Table 3-1 below |  | Ref. 1, Table 3-1, page 25, pdf page 50
Coal Input |  |  |  | 393.1107 | 562.1933 | kg/MWh |  | Calculating coal input requirements as if feedstock were Illinois #6 coal
Coal input is not Illinois #6 so input quantity will be adjusted as if feedstock were Illinois #6
Assuming coal input is equivalent to Illinois #6: |  |  |  |  | HHV = 11666 Btu/lb |  | Ref 6, Exhibit 2-3
Ref. 1, Table 3-1, page 25, pdf page 50
Water Use
|  | Without CCS |  | With CCS
Water withdrawal |  | 663.8 | gal/MWh | 1161.8928 | gal/MWh |  |  | Source: Reference [2] |  | Tables 7-5 and 7-6 on page 68, pdf page 83, Table 7-9 on page 71, pdf page 86 Highlighted
|  | 175.3574 | L/MWh | 306.9396 | L/MWh
|  | 11.0633 | gpm/MWnet | 19.3649 | gpm/MWnet
Water discharge |  | 149.5 | gal/MWh | 261.6797 | gal/MWh
|  | 39.4937 | L/MWh | 69.1285 | L/MWh
In Reference [5], water withdrawal and discharge for the subcritical pulverized coal plant with CCS were roughly double that of the PC plant
without CCS. In this analysis, water withdrawal for the PC plant with CCS is about 1.75 x that of the plant without CCS. To scale the water discharge,
the without CCS discharge rate is mutliplied by the ratio of water withdrawals (~1.75x).
From Ref 1 Table 3-21: Additional water requirement for CCS |  |  |  |  | Page 49 pdf 74
|  |  |  | For 90% CCS |  | Net output (MW)
Water makeup to Amine Plant, gpm |  |  |  | 427 | gpm | 303.317
|  |  |  | 84.4661 | gal/MWh
Water makeup to Cooling Tower, gpm |  |  |  | 2091 | gpm
|  |  |  | 413.6267 | gal/MWh
Advanced Amine Plant Performance
Table 3-20 and Table 3-21 compare the amine plant material balance and energy demands,
respectively, for each recovery case. The material balance shown in Table 3-20 is for the
complete amine plant, as is Table 3-21.
Replacement Power |  |  | Net plant power is going to drop from 433.778 MW to 303.317 MW due to CCS power requirement. The modeling assumes the power will be replaced. The approach is to calculate the replacement energy on a MWh basis at a capacity factor of .85 as per Ref [1].
Source: Reference [1], p ES-3
|  |  | Base Case |  | 90% Capture |  | Difference in plant output
Net Plant Power (kW) |  |  | 433778 |  | 303317 |  | 130461 | kW
Net Plant Power (MW) |  |  | 433.778 |  | 303.317 | MW | 130.461 | MW
Net MWhrs at .85 Cap Factor |  |  | 3232123.2558 |  | 2260045.2987 |  | 972077.9571 | MWhrs
[7 empty] | 0.43011 | MWh's replaced per MWh generated

## Study Data-CO2
CO2 Emissions for Study Base Case (No CCS)
Source: Reference [1], p ES-3
[5 empty] | 433778 | 303317
net MWh * capacity factor = | 368.7113 | MWh | Base case net * .85
w/o CCS | lb/hr | lb/MWh | kg/MWh
CO2 emissions | 866102 | 2348.9977 | 1065.4874 | Conversion factor (1 kg = 2.204622 lb)

## Conversions
Conversions
Conversion Factors |  |  |  | References
1 | ton | 907.1847 | kg
1 | kg | 2.2046 | lbm
1 | GWh | 1000 | MWh
1 | l | 0.26417 | gal
1 | year | 8766 | hours

## Assumptions
Assumptions
Assumption # | Description
1 | Water withdrawal is 50% ground, 50% surface water.